## Sheet1
round | query_rfi_ref | query_project | query_trade | query_phase | query_text | match_rfi_ref | match_project | match_trade | match_phase | match_text | final_score | keyword_score | semantic_score | phase_score | entity_score | matched_keywords | tier
1 | RFI-1665 | Southline Office | concrete | envelope | REF: Site - Onsite Current Set: L1.20A, 5/L8.01, RFI 1471 POST TO: Site - Onsite Current Set: L1.20A, 5/L8.01 Please review the attached file. The slab of the fire pump room and the generator enclosure at the west of B1 is protruding into the sidewalk at the west of B1. See attached picture for reference. This slab is waterproofed since it is part of the fire water tank. To avoid damaging the waterproofing further, DPR is requesting to chip only the top 4" of the slab/wall to provide a clean lin | RFI-1818 | Southline Office | landscaping, concrete | envelope | REF: Site - Onsite Current Set: L8.05, Site - B2 Current Set: L8.02 POST TO: Site - Onsite Current Set: L8.05, Site - B2 Current Set: L8.02 Please review the attached file. Per discussion with DES, DPR requests clarification on the scope of waterproofing at PSD bioretention areas and B2 terrace walls. All areas highlighted in green on pages 3 and 5 show where waterproofing is accounted for. Please confirm that this scope is correct and that waterproofing is not to be installed on the sidewalk no | 0.8324 | 1 | 0.8854 | 1 | 0 | onsite, waterproofing, detail, site, file, sidewalk, concrete, side, water, dpr, post, line | 1
1 | RFI-124 | CoreSite Data Center | architectural | preconstruction | Per Sheet P3-A04-03, at the East wall of the men's and women's restrooms there will be two grab bars on the existing wall. Please confirm it is acceptable to attach the grab bars backing to the existing wall. This appears to be a shaft wall, but it is unclear if a furred wall was constructed in front of the shaft wall. Suggested answer Corgan, please confirm if proposed is acceptable, and if a furred wall was constructed in front of the shaft wall. | RFI-69 | Abbott Alameda Office TI | architectural, electrical, interior_finishes, mechanical, plumbing | preconstruction | Abbott Alameda 1420 HBP - Phase 1B Restrooms Existing Conditions Modifications Confirmation | 0.8278 | 1 | 0.8502 | 1 | 0 | attach, women, furred, wall, furred wall, men, restrooms, acceptable | 1
1 | RFI-0468.1 | Southline Office | architectural | envelope | Per MCA comments on the waterproofing shop drawings, please confirm it is acceptable to post apply at the pit walls and to terminate the waterproofing on the vertical face wall rather than the thickened portion of the slab. Revised shop drawings were submitted and approved. Please update Sheet | RFI-0974 | Southline Office | architectural | envelope | B2 Below Grade Waterstop at Perimeter Footings | 0.8263 | 1 | 0.8743 | 1 | 0 | shop, waterproofing shop drawings, waterproofing, waterproofing shop, shop drawings, sheet, mca, drawings, acceptable | 1
1 | RFI-180 | CoreSite Data Center | interior_finishes | preconstruction | - Is powder coating the specified finish method? 3) Was the ceiling tile used in the previous phase a proprietary product? | RFI-69 | Abbott Alameda Office TI | architectural, electrical, interior_finishes, mechanical, plumbing | preconstruction | Abbott Alameda 1420 HBP - Phase 1B Restrooms Existing Conditions Modifications Confirmation | 0.8234 | 1 | 0.8353 | 1 | 0 | tile, phase, ceiling, finish | 1
1 | RFI-33 | CoreSite Data Center | architectural | preconstruction | The RCP shows Women & Men's Restroom ceilings @10' 0" and at sink areas-ceiling in RCP shows to be @11'-0". The Architecture Model ceiling height is @10' 0" and sink ceilings @8' 0". Please confirm the ceiling heights near sink area. Suggested answer Please confirm if ceiling height near sink area is 8' 0" above RAF. | RFI-29 | CoreSite Data Center | architectural | preconstruction | As discussed on 5/29/25 BIM Cluster Meeting, bottom of existing supply ductwork at Men's (Restroom) 226 is 9'3". The specified ceiling height per enlarged RCP, 4/P3-A04-03, is 10' above RAF (13' above SOD). Please confirm if the proposed change to the ceiling height in Men's Room 226 is acceptable. Suggested answer Lower ceiling to 8'9" in Men's Room 226 | 0.8226 | 1 | 0.9249 | 1 | 0 | raf, restroom, ceiling, model, men, height, ceiling height, suggested, rcp | 1
1 | RFI-1873 | Southline Office | landscaping | mep_trim_out | REF: Site - Onsite Current Set: L4.20, 12, 13/L8.04, Site - B2 Current Set: L4.10 POST TO: Site - Onsite Current Set: L4.20, Site - B2 Current Set: L4.10 Please review the attached files. Per the lighting plans, up lights are to be installed at several tree locations across the site. Details 12/L8.04 and 13/L8.04 show dimensions on center of the lights for 36" box trees and 60" box trees, but no detail is shown for 48" box trees. Please confirm the dimension for up lights located at 48" box tree | RFI-1501 | Southline Office | electrical, landscaping | mep_trim_out | REF: Site - Onsite Current Set: E1.02 POST TO: Site - Onsite Current Set: E1.02 Please review the attached file. Per conditions in the field, two (2) E3s will need to be shifted in location to not conflict with a storm drain and the bioretention area respectively. Please confirm the proposed changes in locations are acceptable. | 0.8196 | 1 | 0.9449 | 1 | 0 | onsite, detail, locations, lighting, site, post | 1
1 | RFI-1873 | Southline Office | landscaping | mep_trim_out | REF: Site - Onsite Current Set: L4.20, 12, 13/L8.04, Site - B2 Current Set: L4.10 POST TO: Site - Onsite Current Set: L4.20, Site - B2 Current Set: L4.10 Please review the attached files. Per the lighting plans, up lights are to be installed at several tree locations across the site. Details 12/L8.04 and 13/L8.04 show dimensions on center of the lights for 36" box trees and 60" box trees, but no detail is shown for 48" box trees. Please confirm the dimension for up lights located at 48" box tree | RFI-1501 | Southline Office | electrical, landscaping | mep_trim_out | REF: Site - Onsite Current Set: E1.02 POST TO: Site - Onsite Current Set: E1.02 Please review the attached file. Per conditions in the field, two (2) E3s will need to be shifted in location to not conflict with a storm drain and the bioretention area respectively. Please confirm the proposed changes in locations are acceptable. | 0.8196 | 1 | 0.9449 | 1 | 0 | onsite, detail, locations, lighting, site, post | 1
1 | RFI-1751 | Southline Office | architectural, structural | structure | B2 Coffee and Back Bar Shelving Light Rough-In Steel Clarifications 1 B2 Coffee and Back Bar Shelving Question: RFI 1524.1 Response proposes to use z-clips to attach the Back Bar and Coffee Bar steel shelves to the wall. Per meeting between DPR/Sprig/Glazier, the z-clip solutio | RFI-0890 | Southline Office | architectural, structural | structure | Would 1 1/2SCH40 pipe (osd 1 7/8") be preferable? | 0.8189 | 1 | 0.9431 | 1 | 0 | attach, wall, steel, back, bar | 1
1 | RFI-124 | CoreSite Data Center | architectural | preconstruction | Per Sheet P3-A04-03, at the East wall of the men's and women's restrooms there will be two grab bars on the existing wall. Please confirm it is acceptable to attach the grab bars backing to the existing wall. This appears to be a shaft wall, but it is unclear if a furred wall was constructed in front of the shaft wall. Suggested answer Corgan, please confirm if proposed is acceptable, and if a furred wall was constructed in front of the shaft wall. | RFI-95 | CoreSite Data Center | architectural, structural | preconstruction | What material should be implemented as a buffer between the new slab and the existing East wall? Can the existing East wall support the loading imposed by the new concrete slab? | 0.8182 | 1 | 0.9059 | 1 | 0 | shaft, east wall, wall, east, men, unclear, suggested, acceptable, corgan | 1
1 | RFI-118 | CoreSite Data Center | fire_protection | preconstruction | At the West wall columns fireproofing will be within the plenum space below the raised access floor. Suggested answer Corgan, please confirm if the project needs to prevent monokote fireproofing form becoming air born within the plenum space. If so, please provide details for framing and drywall, or an alternative solution, such as a monokote sealer. | RFI-147 | CoreSite Data Center | architectural, fire_protection | preconstruction | Per Enlarged Plans P3-A04-01, the North and West walls of Mechanical room 0235A call out for non-rated walls, while per Life Safety Plan P3-G01-03 the North and West wall call out for 1 hour rated fire barrier assembly. Suggested answer Corgan, please confirm if in the Mechanical room 0235A the North and West walls should be 1 hour rated, A6-DA. | 0.817 | 1 | 0.8056 | 1 | 0 | wall, west wall, form, west, suggested, corgan | 1
1 | RFI-0468.1 | Southline Office | architectural | envelope | Per MCA comments on the waterproofing shop drawings, please confirm it is acceptable to post apply at the pit walls and to terminate the waterproofing on the vertical face wall rather than the thickened portion of the slab. Revised shop drawings were submitted and approved. Please update Sheet | RFI-1128 | Southline Office | architectural | envelope | B2 Exterior Skin Waterproofing Details 02, A8.00, A8.01 Question: 1. Per meeting with WW/MCA/BTM/DES/DPR, BTM will be providing a 3x3in GE Elemax 5000 strip per GE warranted detail at all corners (typ.) Please confirm this is acceptable. 2. At typ. Curtainwall sill at Terra Cotta conditions, MCA confirmed it is | 0.8168 | 1 | 0.9359 | 1 | 0 | waterproofing, wall, sheet, mca, acceptable | 1
1 | RFI-1614 | Southline Office | architectural, concrete | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.10A POST TO: Site - B2 Current Set: L1.01, L1.10A No finish is called out on L1.01 of the B2 Site set for concrete paving "P3". In addition, no finish is provided for concrete stairs "ST1" and "ST2". Please review the attached file and confirm the finishes described. If the finishes are not acceptable, please advise. | RFI-1983 | Southline Office | landscaping, architectural | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.11A, L1.11B, L2.10A, L2.10B, L3.10, L4.01, L4.02, L4.10, L4.11 POST TO: Site - B2 Current Set: L1.01, L1.11A, L1.11B, L2.10A, L2.10B, L3.10, L4.01, L4.02, L4.10, L4.11 Please review the attached file. Per the site walk on 9/25/24 and team meeting on 10/09/24, please confirm that the following scope changes to the Building 2 site vegetable garden are valid: Bon Appetit and Farmscape will be taking over the soil, finish irrigation drip lines, and planting mate | 0.816 | 1 | 0.8261 | 1 | 0 | 10a, site, file, finish, post | 1
1 | RFI-0438 | Southline Office | structural | structure | Please confirm if lengthening of C-Channel to main steel support is acceptable. Please confirm if C-Channel to C-Channel connection per detail 17/S5.50 is acceptable at shown location. Please confirm if C-Channel Location is 8'-9 11/16" from Gridline J.2. | RFI-1435 | Southline Office | structural | structure | PSD C Channel Embeds at Tier 6 Remediation Confirmation | 0.8127 | 1 | 0.829 | 1 | 0 | c-channel, acceptable, detail, steel | 1
1 | RFI-1665 | Southline Office | concrete | envelope | REF: Site - Onsite Current Set: L1.20A, 5/L8.01, RFI 1471 POST TO: Site - Onsite Current Set: L1.20A, 5/L8.01 Please review the attached file. The slab of the fire pump room and the generator enclosure at the west of B1 is protruding into the sidewalk at the west of B1. See attached picture for reference. This slab is waterproofed since it is part of the fire water tank. To avoid damaging the waterproofing further, DPR is requesting to chip only the top 4" of the slab/wall to provide a clean lin | RFI-1573 | Southline Office | concrete, plumbing, civil_site | foundation | REF: Site - Onsite Current Set: L8.06 POST TO: Site - Onsite Current Set: L8.06 Currently with what is excavated and graded for the sidewalk retaining wall by the B1 East side loading dock as shown on Detail 5/L8.06, there is a conflict with the 6” sanitary sewer that appears to penetrate the shear key at the bottom of the footing. There will be roughly 3” of clearance on top of the pipe and 6” below the bottom of pipe through the wall. Please provide rebar trim and penetration sleeve details fo | 0.8121 | 1 | 0.9751 | 0.7 | 0 | onsite, detail, 5/l8, site, sidewalk, side, post, top, line | 1
1 | RFI-0438 | Southline Office | structural | structure | Please confirm if lengthening of C-Channel to main steel support is acceptable. Please confirm if C-Channel to C-Channel connection per detail 17/S5.50 is acceptable at shown location. Please confirm if C-Channel Location is 8'-9 11/16" from Gridline J.2. | RFI-1709 | Southline Office | architectural, structural | structure | B2 Structural Steel Support at Bar Drum Wall 01, A9.51, Submittal 4722 Question: The low wall at the rear of the Bar Drum structure currently does not call out any Structural Steel low wall supports. Please confirm if the wall requires HSS tube steel similar to what is submitted on 4722 B2 GS Servery Win | 0.811 | 1 | 0.8175 | 1 | 0 | steel support, support, detail, steel | 1
1 | RFI-1665 | Southline Office | concrete | envelope | REF: Site - Onsite Current Set: L1.20A, 5/L8.01, RFI 1471 POST TO: Site - Onsite Current Set: L1.20A, 5/L8.01 Please review the attached file. The slab of the fire pump room and the generator enclosure at the west of B1 is protruding into the sidewalk at the west of B1. See attached picture for reference. This slab is waterproofed since it is part of the fire water tank. To avoid damaging the waterproofing further, DPR is requesting to chip only the top 4" of the slab/wall to provide a clean lin | RFI-1808 | Southline Office | civil_site, concrete, landscaping | structure | REF: Site - Onsite Current Set: C3.2 POST TO: Site - Onsite Current Set: C3.2 Please reference the attached files. Per DES and DPR field walk on 07/16/24, the top of curb terminating at the loading dock of Parking Structure D has an elevation 6 inches below the building slab. Per discussion between DES, BKF and DPR on 07/18/24, this curb is to be demolished and given new dimensions. DPR recommends raising the curb to have a top elevation of 23.50 so it is flush with building slab and removing th | 0.8102 | 1 | 0.8866 | 0.85 | 0 | slab, onsite, detail, site, file, sidewalk, concrete, side, west, dpr, post, top | 1
1 | RFI-1873 | Southline Office | landscaping | mep_trim_out | REF: Site - Onsite Current Set: L4.20, 12, 13/L8.04, Site - B2 Current Set: L4.10 POST TO: Site - Onsite Current Set: L4.20, Site - B2 Current Set: L4.10 Please review the attached files. Per the lighting plans, up lights are to be installed at several tree locations across the site. Details 12/L8.04 and 13/L8.04 show dimensions on center of the lights for 36" box trees and 60" box trees, but no detail is shown for 48" box trees. Please confirm the dimension for up lights located at 48" box tree | RFI-1618 | Southline Office | architectural, concrete, landscaping, electrical | mep_trim_out | REF: Site - Onsite Current Set: L1.21A, Submittal #4393 POST TO: Site - Onsite Current Set: L1.21A Please review the attached file. Per constructability meeting on 4/23/24, DPR noted that the E13 linear light fixtures are to have 3/8" tolerance within the blockout within the concrete paving. Please confirm the following: 1. The 3/8" gap between light and concrete will be filled with polymeric sand. 2. Please review the mark-up on the following page and provide responses to each light condition. | 0.8067 | 1 | 0.8058 | 1 | 0 | onsite, detail, site, post, within | 2
1 | RFI-124 | CoreSite Data Center | architectural | preconstruction | Per Sheet P3-A04-03, at the East wall of the men's and women's restrooms there will be two grab bars on the existing wall. Please confirm it is acceptable to attach the grab bars backing to the existing wall. This appears to be a shaft wall, but it is unclear if a furred wall was constructed in front of the shaft wall. Suggested answer Corgan, please confirm if proposed is acceptable, and if a furred wall was constructed in front of the shaft wall. | RFI-147 | CoreSite Data Center | architectural, fire_protection | preconstruction | Per Enlarged Plans P3-A04-01, the North and West walls of Mechanical room 0235A call out for non-rated walls, while per Life Safety Plan P3-G01-03 the North and West wall call out for 1 hour rated fire barrier assembly. Suggested answer Corgan, please confirm if in the Mechanical room 0235A the North and West walls should be 1 hour rated, A6-DA. | 0.806 | 0.95 | 0.8273 | 1 | 0 | wall, suggested, corgan | 1
1 | RFI-0468.1 | Southline Office | architectural | envelope | Per MCA comments on the waterproofing shop drawings, please confirm it is acceptable to post apply at the pit walls and to terminate the waterproofing on the vertical face wall rather than the thickened portion of the slab. Revised shop drawings were submitted and approved. Please update Sheet | RFI-1070 | Southline Office | architectural, exterior_envelope | envelope | Background: Details 2/A8.20 and 6/A8.20 show the parapet conditions at the main roof. Per BT Mancini’s shop drawings (SLP1 - 0656-074213-3 B1 Terracotta Shop Drawings), waterproofing on top of the sheathing and below the metal panel coping cap will be GE Elemax 2600. Per previous exterior skin coordination meetings and discussion with DES and MCA, BT Mancini details (as shown in submittal 0656) following the standard GE- warranted detail, showing the additional GE Elemax 5000 liquid flashing ins | 0.806 | 1 | 0.9001 | 1 | 0 | shop, waterproofing, shop drawings, mca, face, drawings | 1
1 | RFI-1153 | Southline Office | architectural | interior_finishes | Per email confirmation from DES on 11/20/23, please confirm it is acceptable to locate the tile base joint @ the midpoint of the floor tile (indicated in the updated drawing). | RFI-1078 | Southline Office | architectural, structural, concrete | interior_finishes | Per coordination with Welker Bros and DES, please confirm it is acceptable to proceed with the construction specialties Pedigrid with recessed deep pit exterior WOM in lieu of the specified Forbo Nuway Tuftiguard on sheet If the proposed Construction Specialties Exterior WOM is acceptable, please update detail 16/ SK1 represents the proposed arrangement of the concrete sidewalk and the slab for the exterior walkoff mat. Please refer to SK1 and provide the additional information requested highlig | 0.8058 | 1 | 0.8059 | 1 | 0 | drawing, acceptable, confirmation, des | 1
1 | RFI-33 | CoreSite Data Center | architectural | preconstruction | The RCP shows Women & Men's Restroom ceilings @10' 0" and at sink areas-ceiling in RCP shows to be @11'-0". The Architecture Model ceiling height is @10' 0" and sink ceilings @8' 0". Please confirm the ceiling heights near sink area. Suggested answer Please confirm if ceiling height near sink area is 8' 0" above RAF. | RFI-69 | Abbott Alameda Office TI | architectural, electrical, interior_finishes, mechanical, plumbing | preconstruction | Abbott Alameda 1420 HBP - Phase 1B Restrooms Existing Conditions Modifications Confirmation | 0.8045 | 1 | 0.7725 | 1 | 0 | restroom, ceiling, women, ceilings, men, height, rcp | 1
1 | RFI-124 | CoreSite Data Center | architectural | preconstruction | Per Sheet P3-A04-03, at the East wall of the men's and women's restrooms there will be two grab bars on the existing wall. Please confirm it is acceptable to attach the grab bars backing to the existing wall. This appears to be a shaft wall, but it is unclear if a furred wall was constructed in front of the shaft wall. Suggested answer Corgan, please confirm if proposed is acceptable, and if a furred wall was constructed in front of the shaft wall. | RFI-192 | CoreSite Data Center | architectural | preconstruction | Drawing P3-A06-36 indicates that the walls for the women's and men's bathrooms are to be installed on SOD (slab-on-deck). Please confirm whether these walls should instead be placed directly on the concrete slab. The estimated weight of each wall, including framing and drywall, is approximately 775 lbs. Please confirm that plumbing fixtures will be supported by carriers, and that only the partitions will be mounted to the walls. Carrier weight details are attached for reference. Additionally, pl | 0.8021 | 1 | 0.8466 | 1 | 0 | attach, women, wall, men, suggested, corgan | 1
1 | RFI-1873 | Southline Office | landscaping | mep_trim_out | REF: Site - Onsite Current Set: L4.20, 12, 13/L8.04, Site - B2 Current Set: L4.10 POST TO: Site - Onsite Current Set: L4.20, Site - B2 Current Set: L4.10 Please review the attached files. Per the lighting plans, up lights are to be installed at several tree locations across the site. Details 12/L8.04 and 13/L8.04 show dimensions on center of the lights for 36" box trees and 60" box trees, but no detail is shown for 48" box trees. Please confirm the dimension for up lights located at 48" box tree | RFI-1672 | Southline Office | lighting, landscaping, electrical | mep_trim_out | REF: Site - Offsite Current Set: C3.1, L1.20 POST TO: Site - Offsite Current Set: L1.20 Please review the attached drawings. Per the demo plan C3.1, two street lights along the Centennial Parklet were removed and stored on site. These lights were not to be reinstalled per streetlighting plans or landscape plans. Per conversation with Randy Chen with the city of SSF, these lights are to be reinstalled to allow for sufficient pedestrian lighting along Centennial Way. Please confirm the proposed lo | 0.7996 | 1 | 0.7807 | 1 | 0 | lights, plans, detail, locations, lighting, site, tree, installed, post, details | 2
1 | RFI-0468.1 | Southline Office | architectural | envelope | Per MCA comments on the waterproofing shop drawings, please confirm it is acceptable to post apply at the pit walls and to terminate the waterproofing on the vertical face wall rather than the thickened portion of the slab. Revised shop drawings were submitted and approved. Please update Sheet | RFI-1327.1 | Southline Office | exterior_envelope, architectural | envelope | PSD Roof Taper Adjustments_R1 1 PSD Roof Taper Adjustments_R1 Reference: SLP1 - RFI 1327.1 - PSD Roof Taper Adjustments_R1 Email Conversation between DES and DPR SLP1 - 3110 -076200-0 PSD Sheet Metal Shop Drawings SLP1 - 3939 -075419-2 PSD PVC Membrane Roofing Taper Layout and Shop Drawing Background: Per conversations with DES, to maintain metal panel coping dimensions | 0.7993 | 1 | 0.7784 | 1 | 0 | shop, waterproofing, wall, shop drawings, sheet, drawings, acceptable | 1
1 | RFI-198 | CoreSite Data Center | electrical | preconstruction | At four (4) locations, the current telecommunications design specifies 4" - 90 degree sweeps from the overhead pull can to the Codecom units. This configuration is not constructible due to conflicts between the ceiling penetration of the straight conduit and the 48" sweep 90, resulting in multiple interferences. We are requesting an exception to utilize a pull can transition at these four (4) locations (clouded yellow in the attached drawing) to route the conduits down into the Codecom units. Th | RFI-146 | CoreSite Data Center | electrical | preconstruction | Per the contract documents, the current design specifies that MV-250-AL and MV-200-AL conductors be run in 6" conduit from the underground sections to the second-story generators (Gens 04, 10, and 12) and to Chiller 05 from the USS. CEI would like to request approval to revise this design to use 6" GRC from the underground up to the bottom of the pull can, located approximately two feet above the generator slabs, and then transition to 4" GRC for the exposed portion of the raceway. The proposed | 0.7989 | 1 | 0.8389 | 1 | 0 | proceed, pull, utilize, installation, specifies, transition, design, high, pull cans, use, conduit, suggested, cans, acceptable, due, approximately | 1
1 | RFI-36 | Intuitive Surgical MOB | architectural | mep_trim_out | Detail 8 on drawing A9.11 call for a Mullion Mate or Equivalent Product for the aluminum partition closure. DPR Drywall provided the Mullion Mate product in "Submittal #092923-01 -Mullion Mate". This submittal was rejected and the Mull It Over (STC 55) product is requested. The delta to change to Mull It Over is $89K. Please confirm the change from the Mullion Mate product to the Mull It Over product. Provide direction if only specific rooms need the Mull It Over product. | RFI-69 | Intuitive Surgical MOB | architectural | mep_trim_out | Partition Termination at Mullion Corner | 0.7981 | 1 | 0.8606 | 1 | 0 | partition, mullion mate, drywall, dpr drywall, dpr, mate, mullion | 1
1 | RFI-0438 | Southline Office | structural | structure | Please confirm if lengthening of C-Channel to main steel support is acceptable. Please confirm if C-Channel to C-Channel connection per detail 17/S5.50 is acceptable at shown location. Please confirm if C-Channel Location is 8'-9 11/16" from Gridline J.2. | RFI-1323 | Southline Office | structural | structure | B1 Service Yard Hole Modification for Embed Anchors Confirmation | 0.7964 | 1 | 0.8681 | 1 | 0 | c-channel, acceptable, detail, steel | 1
1 | RFI-198 | CoreSite Data Center | electrical | preconstruction | At four (4) locations, the current telecommunications design specifies 4" - 90 degree sweeps from the overhead pull can to the Codecom units. This configuration is not constructible due to conflicts between the ceiling penetration of the straight conduit and the 48" sweep 90, resulting in multiple interferences. We are requesting an exception to utilize a pull can transition at these four (4) locations (clouded yellow in the attached drawing) to route the conduits down into the Codecom units. Th | RFI-187 | CoreSite Data Center | electrical | preconstruction | 1. CEI has identified a discrepancy on the IFC Telecom drawings regarding the elevation of the underground cable tray. Sheet T02-02 calls for the cable tray to be installed 1'-4" below the raised floor, while sheet T02-02B indicates the tray to be 1'-4" AFF (to the bottom of tray). 2. Additionally, CEI is requesting confirmation on the routing of the four (4) horizontal cable tray runs through the Data Room. As currently shown, these trays are located directly beneath server racks, which would p | 0.796 | 1 | 0.8267 | 1 | 0 | drawing, proceed, requesting, advise, allow, directly, suggested, acceptable, four | 1
1 | RFI-124 | CoreSite Data Center | architectural | preconstruction | Per Sheet P3-A04-03, at the East wall of the men's and women's restrooms there will be two grab bars on the existing wall. Please confirm it is acceptable to attach the grab bars backing to the existing wall. This appears to be a shaft wall, but it is unclear if a furred wall was constructed in front of the shaft wall. Suggested answer Corgan, please confirm if proposed is acceptable, and if a furred wall was constructed in front of the shaft wall. | RFI-114 | CoreSite Data Center | architectural, interior_finishes | preconstruction | At Corridor 260 north of the elevator, the existing shaft wall (see attached markup) is off set by 1 3/8" South. Proposed solution is to keep the architectural layout that would have the 1 3/8" off set at the East side of the shaft wall (yellow markup) to match existing conditions. No issues on the West side of the wall (green markup). Note: on the East of the highlighted (yellow) shaft wall, the wall is skewed by 1 1/4", reason why we are proposing to keep the 1 3/8" off set layout. Suggested a | 0.7957 | 1 | 0.8299 | 1 | 0 | shaft, attach, wall, east, shaft wall, men, suggested, acceptable, corgan | 1
1 | RFI-1873 | Southline Office | landscaping | mep_trim_out | REF: Site - Onsite Current Set: L4.20, 12, 13/L8.04, Site - B2 Current Set: L4.10 POST TO: Site - Onsite Current Set: L4.20, Site - B2 Current Set: L4.10 Please review the attached files. Per the lighting plans, up lights are to be installed at several tree locations across the site. Details 12/L8.04 and 13/L8.04 show dimensions on center of the lights for 36" box trees and 60" box trees, but no detail is shown for 48" box trees. Please confirm the dimension for up lights located at 48" box tree | RFI-1417.1 | Southline Office | concrete, landscaping, masonry, electrical | mep_trim_out | REF: Site - B2 Current Set: L1.11A POST TO: Site - B2 Current Set: L1.11A Please review the attached file. Per email correspondence from DES, a new sketch was sent showing the proposed layout for liner LED E13 light fixtures within the paver and concrete pavement areas of the B2 entry plaza. Please confirm the sketch on page 4 is to be used and provide updated drawings. | 0.7957 | 1 | 0.8557 | 1 | 0 | lights, onsite, detail, site, show, post, within | 2
1 | RFI-0018 | Southline Office |  | structure | If we detail the 6 1/4" square plate washer per Detail-4/S5.43, then there is only 3/16" and 7/16" clearance from plate washer to column flange and Stiffener as shown in Model snippet-1. Please review and advise. If we detail a 3'-5" square embed plate and 3'-2" base plate per Detail-4/S5.43, then there is no weld shelf for a 3/8" fillet weld between the shear plate and embed plate as shown in Model snippet-2. Please review and advise. Per Detail-4/S5.43 3'-5" square embed plate is to be detaile | RFI-0014 | Southline Office |  | structure | B1 AB, base plate and plate washer connection clarification | 0.7955 | 1 | 0.8649 | 1 | 0 | base plate, plate, embed, detail, connection, 3/16, clearance, model, square, marked, headed, advise, dimension, column flange, washer, flange, stiffener, 1/2, snippet-1, embed plate, model snippet-1, column, follow, acceptable, plate washer, 8/s5, anchor, base, understand, length | 4
1 | RFI-1892 | Southline Office | architectural, structural | foundation | B2 Floor Uniformity and Flatness Confirmation 3, Spec Sections 03-3000.3.6 Question: Per the Polished Concrete Mockup Review held on May 15th between PMA/DES/DPR, it was confirmed (see email attached) that the mockup reviewed was the final selection for the concrete uniformity and resolves any floor fl | RFI-1565 | Southline Office | architectural, concrete, landscaping | foundation | Onsite - B1 Plaza Walk-off Mat + ADA Bollard Footing 21A, RFI 1078, Submittal #4175 POST TO: Site - Onsite Current Set: L1.21A Please review the attached files. Per constructability meeting on 4/3/24, DES and DPR discussed the concrete slab below the Building 1 walk-off mats and their f | 0.7946 | 0.95 | 0.8253 | 1 | 0 | final, concrete, floor | 1
1 | RFI-0468.1 | Southline Office | architectural | envelope | Per MCA comments on the waterproofing shop drawings, please confirm it is acceptable to post apply at the pit walls and to terminate the waterproofing on the vertical face wall rather than the thickened portion of the slab. Revised shop drawings were submitted and approved. Please update Sheet | RFI-2003 | Southline Office | exterior_envelope, architectural | envelope | B1 Waterproofing Detail at Loading Dock and CMU Wall Intersection Confirmation 20 Markup | 0.7941 | 1 | 0.8453 | 1 | 0 | waterproofing, wall, sheet, mca | 2
1 | RFI-104 | CoreSite Data Center | mechanical | preconstruction | Construction and temperatures are not indicated for the ESS duct run. Please confirm that ESS duct run shall be constructed of stainless steel welded duct with expansion bellows to account for thermal expansion of high temp air. See highlighted Reference document attached. Please provide schedule for control dampers associated with this scope delineating who is responsible for actuators. Suggested answer Please confirm that ESS duct run shall be constructed of stainless steel welded duct with ex | RFI-69 | Abbott Alameda Office TI | architectural, electrical, interior_finishes, mechanical, plumbing | preconstruction | Abbott Alameda 1420 HBP - Phase 1B Restrooms Existing Conditions Modifications Confirmation | 0.7908 | 1 | 0.7268 | 1 | 0 | scope, ess, duct, air, run | 1
1 | RFI-1751 | Southline Office | architectural, structural | structure | B2 Coffee and Back Bar Shelving Light Rough-In Steel Clarifications 1 B2 Coffee and Back Bar Shelving Question: RFI 1524.1 Response proposes to use z-clips to attach the Back Bar and Coffee Bar steel shelves to the wall. Per meeting between DPR/Sprig/Glazier, the z-clip solutio | RFI-1355 | Southline Office | architectural | structure | Sheets: A4.01, A7.01, A9.13, RFI 1280 RFI 1280 changed the location of the west mechoshade pocket in the L1 lobby. The drop soffits for the mechoshade and light do not align with the current called out dimensions for the wall around the column at X20/ XD. It appears the best way for these soffits and column to align is to shrink the wall around the soffit two directions. Please see dimensions on the next sheet and confirm if it is acceptable to change the column wall to align these lobby soffits | 0.7903 | 1 | 0.7543 | 1 | 0 | attach, wall, steel, light | 2
1 | RFI-118 | CoreSite Data Center | fire_protection | preconstruction | At the West wall columns fireproofing will be within the plenum space below the raised access floor. Suggested answer Corgan, please confirm if the project needs to prevent monokote fireproofing form becoming air born within the plenum space. If so, please provide details for framing and drywall, or an alternative solution, such as a monokote sealer. | RFI-147.1 | CoreSite Data Center | architectural, fire_protection | preconstruction | Per RFI 147: Per Enlarged Plans P3-A04-01, the North and West walls of Mechanical room 0235A call out for non-rated walls, while per Life Safety Plan P3-G01-03 the North and West wall call out for 1 hour rated fire barrier assembly. Confirmed the wall to be A6-D Suggested answer Corgan, please clarify what the hourly fire rating should be. | 0.7902 | 1 | 0.8094 | 1 | 0 | wall, west wall, form, west, suggested, corgan | 1
1 | RFI-1751 | Southline Office | architectural, structural | structure | B2 Coffee and Back Bar Shelving Light Rough-In Steel Clarifications 1 B2 Coffee and Back Bar Shelving Question: RFI 1524.1 Response proposes to use z-clips to attach the Back Bar and Coffee Bar steel shelves to the wall. Per meeting between DPR/Sprig/Glazier, the z-clip solutio | RFI-1879 | Southline Office | architectural | structure | B2 Mod Bar Added Wall due to Plumbing Lines 03, A9.73 Question: Please see photos on the next page. Along 5 line just south of GL B/5 there are four plumbing pipes that are out of the Trimark food service die walls. It seems the best way to encase them into the bar drum is to build a new pony wall under | 0.7879 | 0.95 | 0.7933 | 1 | 0 | wall, steel, bar | 2
1 | RFI-0438 | Southline Office | structural | structure | Please confirm if lengthening of C-Channel to main steel support is acceptable. Please confirm if C-Channel to C-Channel connection per detail 17/S5.50 is acceptable at shown location. Please confirm if C-Channel Location is 8'-9 11/16" from Gridline J.2. | RFI-0451 | Southline Office | structural, concrete | structure | Please confirm the size of the concrete beam encasement and confirm the proposed beam size dimensions. Please confirm the tie size and configuration for the beam encasement and which ties are required per this detail. It is suggested this detail be used and resized to fit the beam. Once area is poured the formwork will be stripped and the bottom will be in filled with native soil slurry. Please confirm that the supporting formwork (2x4 supporting plywood, edge formwork, and 3" concrete dobies) i | 0.7879 | 1 | 0.8396 | 1 | 0 | acceptable, support, detail, steel | 1
1 | RFI-0438 | Southline Office | structural | structure | Please confirm if lengthening of C-Channel to main steel support is acceptable. Please confirm if C-Channel to C-Channel connection per detail 17/S5.50 is acceptable at shown location. Please confirm if C-Channel Location is 8'-9 11/16" from Gridline J.2. | RFI-0889 | Southline Office | structural, architectural | structure | Please advise if U-Edging should be stainless steel or carbon steel (blackened? How are the mesh panels to be fixed to the supporting steel? 51, is it still required? | 0.7871 | 1 | 0.837 | 1 | 0 | location, support, detail, steel | 1
1 | RFI-1147 | Southline Office | concrete, structural |  | B2 GL 12 TOW Threaded Rod Diameter Confirmation 1, RFI 1047 B2 GL 12 TOW Embed Remediation Question: There is rebar obstruction for full embedment of 1" threaded rod on TOW Embed Remediation fix on GL 12. See attached photo depicting the bars that are in question - protruding above the rest. Please co | RFI-1082 | Southline Office | concrete, structural |  | B2 GL 12 Shear Wall TOW Oversized Holes 3, Hilti RE 500 V3 Details, RFI 1047 B2 Gridline 12 TOW Shearwall Embed Remediation Question: The holes for the ¾” epoxy embed at the TOW on grid line 12 have been drilled to 1-1/8” diameter x 37” depth. Grade 55 threaded rods have been epoxied in using HILTI HIT – RE 50 | 0.784 | 1 | 0.9834 | 0.5 | 0 | threaded, b2 gl 12, gl 12, diameter, embed, b2 gl, remediation, rod, 12 tow, tow, embed remediation | 1
1 | RFI-1153 | Southline Office | architectural | interior_finishes | Per email confirmation from DES on 11/20/23, please confirm it is acceptable to locate the tile base joint @ the midpoint of the floor tile (indicated in the updated drawing). | RFI-2030 | Southline Office | architectural | interior_finishes | PSD North and Loading Dock Standpipe Color Confirmation 01 Question: Per email conversations with DES, please confirm that it is acceptable to paint t | 0.7839 | 1 | 0.7169 | 1 | 0 | acceptable, email, confirmation, des | 1
1 | RFI-1665 | Southline Office | concrete | envelope | REF: Site - Onsite Current Set: L1.20A, 5/L8.01, RFI 1471 POST TO: Site - Onsite Current Set: L1.20A, 5/L8.01 Please review the attached file. The slab of the fire pump room and the generator enclosure at the west of B1 is protruding into the sidewalk at the west of B1. See attached picture for reference. This slab is waterproofed since it is part of the fire water tank. To avoid damaging the waterproofing further, DPR is requesting to chip only the top 4" of the slab/wall to provide a clean lin | RFI-1489.1 | Southline Office | concrete, landscaping | foundation | REF: Site - Onsite Current Set: C2.2, L1.20A POST TO: Site - Onsite Current Set: C2.2, L1.20A Please review the attached file. Per the response to RFI 1489, the metal bollards installed at the entrance of the B1 loading dock are to have a concrete footing. Per the horizontal plan C1.1, these bollards overlap with the curb and gutter of the driveway. Currently, the retaining wall is built and the driveway has not been graded yet, as shown in the photos attached. Please provide a detail for how th | 0.7815 | 1 | 0.8724 | 0.7 | 0 | onsite, detail, site, file, concrete, 20a, post | 1
1 | RFI-104 | CoreSite Data Center | mechanical | preconstruction | Construction and temperatures are not indicated for the ESS duct run. Please confirm that ESS duct run shall be constructed of stainless steel welded duct with expansion bellows to account for thermal expansion of high temp air. See highlighted Reference document attached. Please provide schedule for control dampers associated with this scope delineating who is responsible for actuators. Suggested answer Please confirm that ESS duct run shall be constructed of stainless steel welded duct with ex | RFI-56 | CoreSite Data Center | architectural, mechanical | preconstruction | A 24"x22" ESS duct is to be installed at along corridor 262 to purge air from UPS rooms to the building exterior. Existing 16" CHW piping running above restricts duct from being raised to avoid clash with existing branch selector unit and maintaining 9' OH clear height. Additionally, existing CHW line and duct runs at North end of Corridor 262 will exceed available space at wall above door 246B. DPR/SVM propose shifting door 246B plan East below RAF stairs to avoid clash with door frame. Per 6/2 | 0.7788 | 1 | 0.7777 | 1 | 0 | ess, duct run, duct, ess duct, air, suggested, run | 1
1 | RFI-0018 | Southline Office |  | structure | If we detail the 6 1/4" square plate washer per Detail-4/S5.43, then there is only 3/16" and 7/16" clearance from plate washer to column flange and Stiffener as shown in Model snippet-1. Please review and advise. If we detail a 3'-5" square embed plate and 3'-2" base plate per Detail-4/S5.43, then there is no weld shelf for a 3/8" fillet weld between the shear plate and embed plate as shown in Model snippet-2. Please review and advise. Per Detail-4/S5.43 3'-5" square embed plate is to be detaile | RFI-0033 | Southline Office |  | structure | is acceptable, Please confirm the same weld can be applied for stiffener to base plate in Detail-8/S5.43, as the stiffener to base plate weld is missing. 3. Detail-8/S5.43 does not show the weld details for stiffener to column flange. Please furnish the weld. 4. We understand that the Headed studs are to stop at concrete pedestal (top of Base plate to top of concrete pedestal). Please confirm or advise if these are required up to Level-1 Slab. 5. We understand that the 12" concrete perimeter cur | 0.7784 | 1 | 0.8079 | 1 | 0 | base plate, plate, stud, embed, detail, connection, shear plate, clearance, model, marked, headed, advise, column flange, flange, stiffener, grid, weld, snippet-1, detail-8/s5, embed plate, model snippet-1, column, acceptable, 8/s5, model snippet-2, anchor, snippet-2, base, shear, understand | 4
1 | RFI-1751 | Southline Office | architectural, structural | structure | B2 Coffee and Back Bar Shelving Light Rough-In Steel Clarifications 1 B2 Coffee and Back Bar Shelving Question: RFI 1524.1 Response proposes to use z-clips to attach the Back Bar and Coffee Bar steel shelves to the wall. Per meeting between DPR/Sprig/Glazier, the z-clip solutio | RFI-0889 | Southline Office | structural, architectural | structure | Please advise if U-Edging should be stainless steel or carbon steel (blackened? How are the mesh panels to be fixed to the supporting steel? 51, is it still required? | 0.7772 | 1 | 0.8039 | 1 | 0 | attach, steel, light, use, bar | 2
1 | RFI-1751 | Southline Office | architectural, structural | structure | B2 Coffee and Back Bar Shelving Light Rough-In Steel Clarifications 1 B2 Coffee and Back Bar Shelving Question: RFI 1524.1 Response proposes to use z-clips to attach the Back Bar and Coffee Bar steel shelves to the wall. Per meeting between DPR/Sprig/Glazier, the z-clip solutio | RFI-1524.1 | Southline Office | architectural, electrical, structural |  | Please provide updated mounting details for the revised and added wall-mounted shelving via Z-clips at Coffee and Bar back walls. | 0.7763 | 1 | 0.9566 | 0.5 | 0 | coffee, shelving, bar shelving, wall, b2 coffee, back, bar | 1
1 | RFI-198 | CoreSite Data Center | electrical | preconstruction | At four (4) locations, the current telecommunications design specifies 4" - 90 degree sweeps from the overhead pull can to the Codecom units. This configuration is not constructible due to conflicts between the ceiling penetration of the straight conduit and the 48" sweep 90, resulting in multiple interferences. We are requesting an exception to utilize a pull can transition at these four (4) locations (clouded yellow in the attached drawing) to route the conduits down into the Codecom units. Th | RFI-152.1 | CoreSite Data Center | electrical | preconstruction | RFI 152 proposed installation of lighting control MSTP and CAT6 cable as free air in areas with drop ceilings. The design team returned the RFI with direction to maintain all lighting control cabling in conduit. According to the referenced correspondence excerpt, CoreSite has confirmed that free-air installation of MSTP and CAT6 cabling in ceiling areas is acceptable, provided that a cost deduct is applied, the cable is plenum rated, and it is attached to ceiling rods rather than laid on the cei | 0.7758 | 1 | 0.6671 | 1 | 0 | ceiling, installation, design, conduit, suggested, acceptable | 2
1 | RFI-1614 | Southline Office | architectural, concrete | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.10A POST TO: Site - B2 Current Set: L1.01, L1.10A No finish is called out on L1.01 of the B2 Site set for concrete paving "P3". In addition, no finish is provided for concrete stairs "ST1" and "ST2". Please review the attached file and confirm the finishes described. If the finishes are not acceptable, please advise. | RFI-1698 | Southline Office | architectural | interior_finishes | B1 Exterior Penthouse Doors Threshold Confirmation 20 and detail 15/A9.22 Post on: 15/A9.22 Background: Due to the concrete curbs being poured short at the exterior doors in the North and South Penthouse, sill detail 15/A9.22 is n | 0.7753 | 0.95 | 0.7573 | 1 | 0 | concrete, acceptable, post | 2
1 | RFI-1665 | Southline Office | concrete | envelope | REF: Site - Onsite Current Set: L1.20A, 5/L8.01, RFI 1471 POST TO: Site - Onsite Current Set: L1.20A, 5/L8.01 Please review the attached file. The slab of the fire pump room and the generator enclosure at the west of B1 is protruding into the sidewalk at the west of B1. See attached picture for reference. This slab is waterproofed since it is part of the fire water tank. To avoid damaging the waterproofing further, DPR is requesting to chip only the top 4" of the slab/wall to provide a clean lin | RFI-2023 | Southline Office | civil_site, concrete, signage | structure | REF: Site - Onsite Current Set: C2.12, L1.20A, L1.30A POST TO: Site - Onsite Current Set: C2.12 Please review the attached file. Striping plan C2.12 shows 12" white striping bands to be painted on each side of the concrete crosswalks connecting Building 1 and Parking Structure D. However, this striping is not reflected on the landscaping plans. Per the email correspondence on 10/28/24, the 12" white painted striping is to be removed from the crosswalks. Please confirm this is acceptable. | 0.7737 | 1 | 0.8513 | 0.85 | 0 | onsite, detail, site, file, concrete, side, 20a, acceptable, post | 1
1 | RFI-118 | CoreSite Data Center | fire_protection | preconstruction | At the West wall columns fireproofing will be within the plenum space below the raised access floor. Suggested answer Corgan, please confirm if the project needs to prevent monokote fireproofing form becoming air born within the plenum space. If so, please provide details for framing and drywall, or an alternative solution, such as a monokote sealer. | RFI-76 | CoreSite Data Center | drywall | preconstruction | Per 7/7 Workshop, DPR requested a termination detail for the East end of UPS Room walls running E-W. Corgan confirmed that these walls will need to run to interior face of exterior walls to maintain required fire rating instead of terminating at existing drywall. This includes wall separating UPS Room 2C and 2D near GL 5; new UPS Room wall must run through shaft to interior face of exterior wall. Please note, demo of existing drywall at UPS room wall terminations will be required to satisfy requ | 0.7734 | 1 | 0.6647 | 1 | 0 | wall, drywall, form, suggested, corgan | 3
1 | RFI-198 | CoreSite Data Center | electrical | preconstruction | At four (4) locations, the current telecommunications design specifies 4" - 90 degree sweeps from the overhead pull can to the Codecom units. This configuration is not constructible due to conflicts between the ceiling penetration of the straight conduit and the 48" sweep 90, resulting in multiple interferences. We are requesting an exception to utilize a pull can transition at these four (4) locations (clouded yellow in the attached drawing) to route the conduits down into the Codecom units. Th | RFI-69 | Abbott Alameda Office TI | architectural, electrical, interior_finishes, mechanical, plumbing | preconstruction | Abbott Alameda 1420 HBP - Phase 1B Restrooms Existing Conditions Modifications Confirmation | 0.7733 | 1 | 0.6685 | 1 | 0 | drawing, proceed, ceiling, pull, utilize, installation, exception, required, conduit, acceptable | 2
1 | RFI-36 | Intuitive Surgical MOB | architectural | mep_trim_out | Detail 8 on drawing A9.11 call for a Mullion Mate or Equivalent Product for the aluminum partition closure. DPR Drywall provided the Mullion Mate product in "Submittal #092923-01 -Mullion Mate". This submittal was rejected and the Mull It Over (STC 55) product is requested. The delta to change to Mull It Over is $89K. Please confirm the change from the Mullion Mate product to the Mull It Over product. Provide direction if only specific rooms need the Mull It Over product. | RFI-1172 | Southline Office | architectural | mep_trim_out | B2 - Lighting Inverter Room 01, California Fire Code Chapter 12 Section 1207 California Fire Code chapter 12 Section 1207.7.4 calls for 2-hour fire-resistance rated separation for electrical energy storage systems (ESS). The lighting inverter is considered an electrical energy storage syst | 0.7718 | 1 | 0.6928 | 1 | 0 | detail, call, closure, product | 1
1 | RFI-0503.1 | Southline Office | structural |  | PSD CMU Support Embeds Confirmation_R1 | RFI-0535.1 | Southline Office | structural | structure | Please confirm it is acceptable to relocate 12" NB CMU Wall to be aligned with the west side of T3 beam. MEPF has been coordinated and no | 0.7713 | 1 | 1.0342 | 0.5 | 0 | support embeds, psd, psd cmu, cmu support, embeds, psd cmu support, cmu support embeds, support, cmu | 1
1 | RFI-1614 | Southline Office | architectural, concrete | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.10A POST TO: Site - B2 Current Set: L1.01, L1.10A No finish is called out on L1.01 of the B2 Site set for concrete paving "P3". In addition, no finish is provided for concrete stairs "ST1" and "ST2". Please review the attached file and confirm the finishes described. If the finishes are not acceptable, please advise. | RFI-0855.1 | Southline Office | structural, architectural | interior_finishes | Please verify that at these wing walls, the posts are only required at the end? | 0.7711 | 0.95 | 0.7487 | 1 | 0 | advise, addition, post | 2
1 | RFI-0040 | Southline Office |  | structure | B1 encased beam backup bar and weld at bottom flange | RFI-0017 | Southline Office | structural | structure | B1 Backup Bar and Run-off Tab Requirements for Moment and Framed Beams | 0.7697 | 1 | 0.7792 | 1 | 0 | bottom, beam, flange, backup bar, backup, bottom flange, bar, weld | 4
1 | RFI-0040 | Southline Office |  | structure | B1 encased beam backup bar and weld at bottom flange | RFI-0017 | Southline Office | structural | structure | B1 Backup Bar and Run-off Tab Requirements for Moment and Framed Beams | 0.7697 | 1 | 0.7792 | 1 | 0 | bottom, beam, flange, backup bar, backup, bottom flange, bar, weld | 4
1 | RFI-33 | CoreSite Data Center | architectural | preconstruction | The RCP shows Women & Men's Restroom ceilings @10' 0" and at sink areas-ceiling in RCP shows to be @11'-0". The Architecture Model ceiling height is @10' 0" and sink ceilings @8' 0". Please confirm the ceiling heights near sink area. Suggested answer Please confirm if ceiling height near sink area is 8' 0" above RAF. | RFI-62.1 | CoreSite Data Center | architectural | preconstruction | Per RFIs 34 and 47, the segmented area of ACT ceiling in corridor 260 between door 260 and door 262 will need to be lowered to 9' 8" to accommodate existing overhead conditions. The updated RCP issued by Corgan via RFI 62 response reflects these updates. However, the updated RCP does not specify the transition condition between the 11' ceiling and 9'8" ceiling in Corridor 260A. Per a BIM cluster call, a bulkhead soffit was proposed by DPR and verbally confirmed by Corgan. Suggested answer Corgan | 0.7697 | 1 | 0.649 | 1 | 0 | heights, ceiling, area, ceiling heights, model, men, height, ceiling height, suggested, rcp | 2
1 | RFI-36 | Intuitive Surgical MOB | architectural | mep_trim_out | Detail 8 on drawing A9.11 call for a Mullion Mate or Equivalent Product for the aluminum partition closure. DPR Drywall provided the Mullion Mate product in "Submittal #092923-01 -Mullion Mate". This submittal was rejected and the Mull It Over (STC 55) product is requested. The delta to change to Mull It Over is $89K. Please confirm the change from the Mullion Mate product to the Mull It Over product. Provide direction if only specific rooms need the Mull It Over product. | RFI-1078 | Southline Office | architectural, structural, concrete | interior_finishes | Per coordination with Welker Bros and DES, please confirm it is acceptable to proceed with the construction specialties Pedigrid with recessed deep pit exterior WOM in lieu of the specified Forbo Nuway Tuftiguard on sheet If the proposed Construction Specialties Exterior WOM is acceptable, please update detail 16/ SK1 represents the proposed arrangement of the concrete sidewalk and the slab for the exterior walkoff mat. Please refer to SK1 and provide the additional information requested highlig | 0.7694 | 1 | 0.7596 | 0.85 | 0 | drawing, detail, change, product, dpr, requested, submittal | 1
1 | RFI-198 | CoreSite Data Center | electrical | preconstruction | At four (4) locations, the current telecommunications design specifies 4" - 90 degree sweeps from the overhead pull can to the Codecom units. This configuration is not constructible due to conflicts between the ceiling penetration of the straight conduit and the 48" sweep 90, resulting in multiple interferences. We are requesting an exception to utilize a pull can transition at these four (4) locations (clouded yellow in the attached drawing) to route the conduits down into the Codecom units. Th | RFI-64 | CoreSite Data Center | electrical, architectural | preconstruction | RPP Clashes discussed with DPR/CEI/Design Teams on 6/24 breakout. These clashes were not resolved during discussion and require design team direction. See referenced markup for locations and identified clashes. 1. Existing CHW lines running directly above proposed RPP cluster at GL F/1-2 2. RPP cluster will clash with existing BRB at GL A/5 These clashes were previously listed in RFI 61, but deferred to separate RFI to capture confirmation of RPP clashes resolved on #61 as discussed on 6/24 brea | 0.768 | 1 | 0.7412 | 1 | 0 | locations, units, design, directly, suggested, acceptable, overhead | 1
1 | RFI-33 | CoreSite Data Center | architectural | preconstruction | The RCP shows Women & Men's Restroom ceilings @10' 0" and at sink areas-ceiling in RCP shows to be @11'-0". The Architecture Model ceiling height is @10' 0" and sink ceilings @8' 0". Please confirm the ceiling heights near sink area. Suggested answer Please confirm if ceiling height near sink area is 8' 0" above RAF. | RFI-72 | CoreSite Data Center | architectural, mechanical, electrical | preconstruction | Duct main running servicing admin space cannot be installed above 11' ceiling at Corridor 260 segment outside of restrooms, see attached markup, due to plumbing above. Bottom of duct support is 11', but the ceiling would need to be lowered at least 6" to 10'-6" to accommodate light fixtures underneath duct. Per 6/26 BIM cluster meeting, it was proposed and confirmed by Corgan that the Corridor 260 ceiling segment should be lowered by an additional 6" to 10' to match restroom ceiling heights. Sug | 0.7669 | 1 | 0.7368 | 1 | 0 | raf, heights, restroom, ceiling, ceiling heights, model, men, height, ceiling height, suggested | 2
1 | RFI-104 | CoreSite Data Center | mechanical | preconstruction | Construction and temperatures are not indicated for the ESS duct run. Please confirm that ESS duct run shall be constructed of stainless steel welded duct with expansion bellows to account for thermal expansion of high temp air. See highlighted Reference document attached. Please provide schedule for control dampers associated with this scope delineating who is responsible for actuators. Suggested answer Please confirm that ESS duct run shall be constructed of stainless steel welded duct with ex | RFI-47 | CoreSite Data Center | electrical, mechanical | preconstruction | Cycle 1 6/23/25: Running duct through the fiber room was flagged as an issue on the 6/18 DPR/design team breakout call. Duct will need to be routed through Corridor 260A around existing conditions. The ceiling heights at duct run will need to be lowered to 10' at some locations and below 10' at other locations of the run accommodate the duct. Ceiling height at Corridor 260A will be 9'8" per RFI #34 and the ceiling height through Corridor 230 and 231 will need to be 10', see referenced markup. -- | 0.7668 | 1 | 0.7374 | 1 | 0 | duct run, duct, air, suggested, run | 1
1 | RFI-0503.1 | Southline Office | structural |  | PSD CMU Support Embeds Confirmation_R1 | RFI-0572 | Southline Office | architectural, concrete, structural |  | Per RFI0341.2 response, South wall of Electrical Room (between G9 and G10) is to be 8" NB Conc. Wall. Per RFI0341.1, embed will still be required at 8" NB Conc. Wall. Please confirm. Per RFI0341.1, 8" NB Conc. Wall is to stop at the Bottom of Level 2 Slab. CMU Wall at Tier 2 & 5 are to remain CMU. Embed supports will be required per RFI0341.1. Please confirm. Please confirm if NB Conc. walls are to receive CMU supports per RFI0341.1 and bearing Conc. Walls (Along G11 and G12) are to use detail 1 | 0.7655 | 1 | 1.0149 | 0.5 | 0 | psd, psd cmu, cmu support, psd cmu support, support, cmu | 1
1 | RFI-104 | CoreSite Data Center | mechanical | preconstruction | Construction and temperatures are not indicated for the ESS duct run. Please confirm that ESS duct run shall be constructed of stainless steel welded duct with expansion bellows to account for thermal expansion of high temp air. See highlighted Reference document attached. Please provide schedule for control dampers associated with this scope delineating who is responsible for actuators. Suggested answer Please confirm that ESS duct run shall be constructed of stainless steel welded duct with ex | RFI-68 | CoreSite Data Center | mechanical | preconstruction | 1. There are a handful of duct runs/registers/FDs/FSDs on the design drawings that are missing sizing/tags. Please provide this information. (See pink markups on Reference document) 2. The grilles in the restrooms currently show as being hard piped. Please confirm we can use flex connections to these grilles. (See green markups on Reference document) Suggested answer 1. Please provide this missing information. (See pink markups on Reference document) 2. Please confirm we can use flex connections | 0.7651 | 1 | 0.7317 | 1 | 0 | duct run, document, duct, suggested, run | 2
1 | RFI-0503.1 | Southline Office | structural |  | PSD CMU Support Embeds Confirmation_R1 | RFI-0535 | Southline Office | structural |  | As per response to DPR RFI #0295.1 on the attached sheet S6.00, CMU Support Embed is to be located 2'-0" from each end of CMU and spaced at 4'-0" O.C. However if the embeds are spaced at 4'-0" O.C., the distance from end of CMU wall will be either more than or less than 2'-0". Thus, please see attached erection drawings AB2450, AB2451, AB2452 & AB2453 and confirm the clouded distance (shaded in yellow) from CL of embed to end of CMU is still acceptable. Otherwise, please advise on the maximum & | 0.7644 | 1 | 1.0114 | 0.5 | 0 | support embeds, psd, psd cmu, cmu support, embeds, psd cmu support, cmu support embeds, support, cmu | 1
1 | RFI-0503.1 | Southline Office | structural |  | PSD CMU Support Embeds Confirmation_R1 | RFI-0295.1 | Southline Office | structural, concrete, architectural | structure | Please confirm if detail 8/S6.00 is to be used for the NB CMU walls highlighted in red on sheet S2.02. If detail 8/S6.00 is to be used for the NB CMU Walls highlighted in red on sheet S2.02, please provide connection details for NB CMU Walls to 2' PT Beam (detail -2) and for NB CMU Walls to 1'-4" PT Beams (detail -1). | 0.7636 | 1 | 1.0085 | 0.5 | 0 | psd, psd cmu, support, cmu | 1
1 | RFI-180 | CoreSite Data Center | interior_finishes | preconstruction | - Is powder coating the specified finish method? 3) Was the ceiling tile used in the previous phase a proprietary product? | RFI-62.1 | CoreSite Data Center | architectural | preconstruction | Per RFIs 34 and 47, the segmented area of ACT ceiling in corridor 260 between door 260 and door 262 will need to be lowered to 9' 8" to accommodate existing overhead conditions. The updated RCP issued by Corgan via RFI 62 response reflects these updates. However, the updated RCP does not specify the transition condition between the 11' ceiling and 9'8" ceiling in Corridor 260A. Per a BIM cluster call, a bulkhead soffit was proposed by DPR and verbally confirmed by Corgan. Suggested answer Corgan | 0.7628 | 0.95 | 0.6844 | 1 | 0 | ceiling tile, tile, ceiling | 3
1 | RFI-36 | Intuitive Surgical MOB | architectural | mep_trim_out | Detail 8 on drawing A9.11 call for a Mullion Mate or Equivalent Product for the aluminum partition closure. DPR Drywall provided the Mullion Mate product in "Submittal #092923-01 -Mullion Mate". This submittal was rejected and the Mull It Over (STC 55) product is requested. The delta to change to Mull It Over is $89K. Please confirm the change from the Mullion Mate product to the Mull It Over product. Provide direction if only specific rooms need the Mull It Over product. | RFI-121 | Intuitive Surgical MOB | architectural | mep_trim_out | Exit Passageway 1066 Mull-it-over Location Exit Passageway 1066 Mull-it-over Location Reference: Attached RFI Form/ Level 1/A2.11 Question: Current drawings have exit passageway 1066 south wall terminating to glass. Per Mull-it-over, the UL cannot terminate to glass and requires a vertical mullion to maintain fire rating. Please confirm this wall can be extended 41" south to terminate at the vertical mullion and maintain a fire rating. | 0.7619 | 0.95 | 0.7723 | 1 | 0 | drawing, detail, mullion | 2
1 | RFI-33 | CoreSite Data Center | architectural | preconstruction | The RCP shows Women & Men's Restroom ceilings @10' 0" and at sink areas-ceiling in RCP shows to be @11'-0". The Architecture Model ceiling height is @10' 0" and sink ceilings @8' 0". Please confirm the ceiling heights near sink area. Suggested answer Please confirm if ceiling height near sink area is 8' 0" above RAF. | RFI-15 | CoreSite Data Center | architectural | preconstruction | Per RFP RFI-40, please provide a section through at the soffit at the North side of the womens (225) restroom, south side of the mens (226) restroom as well as the North side of the hallway outside these rooms. Reference detail 4/P3-A04-03 | 0.7618 | 0.95 | 0.7812 | 1 | 0 | restroom, women, men | 1
1 | RFI-0503.1 | Southline Office | structural |  | PSD CMU Support Embeds Confirmation_R1 | RFI-1061.1 | Southline Office | structural | structure | PSD CMU Embeds on Gridline GD Location Confirmation_R1 1 PSD CMU Embeds on Gridline GD Location Confirmation_R1 Reference: SLP1 - RFI 1061.1 - PSD CMU Embeds on Gridline GD Location Confirmation_R1 SLP1 - RFI1061 - PSD CMU Embeds on Gridline GD Location Confirmation Post on: S2.03 Background: On RFI 1061, the markup did not show the accurate location of the CMU wall in rel | 0.7616 | 1 | 1.002 | 0.5 | 0 | confirmation_r1, psd, psd cmu, cmu support, embeds, support, cmu | 1
1 | RFI-1614 | Southline Office | architectural, concrete | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.10A POST TO: Site - B2 Current Set: L1.01, L1.10A No finish is called out on L1.01 of the B2 Site set for concrete paving "P3". In addition, no finish is provided for concrete stairs "ST1" and "ST2". Please review the attached file and confirm the finishes described. If the finishes are not acceptable, please advise. | RFI-0635.2 | Southline Office | architectural | interior_finishes | B2 Concrete Finish Clarification | 0.7604 | 0.95 | 0.8064 | 1 | 0 | concrete, finish, acceptable | 2
1 | RFI-104 | CoreSite Data Center | mechanical | preconstruction | Construction and temperatures are not indicated for the ESS duct run. Please confirm that ESS duct run shall be constructed of stainless steel welded duct with expansion bellows to account for thermal expansion of high temp air. See highlighted Reference document attached. Please provide schedule for control dampers associated with this scope delineating who is responsible for actuators. Suggested answer Please confirm that ESS duct run shall be constructed of stainless steel welded duct with ex | RFI-53 | CoreSite Data Center | architectural, mechanical | preconstruction | #0242 UPS Room 2B - AR Furring wall clashes with Existing Duct. There is limited space for framing the furring wall between the duct and steel column. Need confirmation if the wall can be framed up to below the the existing duct. Reference Newforma issue #68. Suggested answer Corgan, please confirm it is acceptable to frame the furred wall in UPS Room 242 below the existing transfer duct to exterior per the attached markup as tight as possible. | 0.7603 | 0.95 | 0.7742 | 1 | 0 | duct, suggested, steel | 1
1 | RFI-36 | Intuitive Surgical MOB | architectural | mep_trim_out | Detail 8 on drawing A9.11 call for a Mullion Mate or Equivalent Product for the aluminum partition closure. DPR Drywall provided the Mullion Mate product in "Submittal #092923-01 -Mullion Mate". This submittal was rejected and the Mull It Over (STC 55) product is requested. The delta to change to Mull It Over is $89K. Please confirm the change from the Mullion Mate product to the Mull It Over product. Provide direction if only specific rooms need the Mull It Over product. | RFI-28 | Intuitive Surgical MOB | architectural | mep_trim_out | Does storefront system tie into a stud drop? | 0.7599 | 0.95 | 0.7956 | 1 | 0 | detail, rooms, dpr | 2
1 | RFI-1614 | Southline Office | architectural, concrete | interior_finishes | REF: Site - B2 Current Set: L1.01, L1.10A POST TO: Site - B2 Current Set: L1.01, L1.10A No finish is called out on L1.01 of the B2 Site set for concrete paving "P3". In addition, no finish is provided for concrete stairs "ST1" and "ST2". Please review the attached file and confirm the finishes described. If the finishes are not acceptable, please advise. | RFI-1440 | Southline Office | architectural, electrical, landscaping, civil_site |  | REF: Site - B2 Current Set: E1.00 POST TO: Site - B2 Current Set: E1.00 Please review the attached file. Please confirm with no exception the B2 Site Photometric Study as designed per the coordination meeting between Silverman, Sprig, DPR, DES and HLB. | 0.7599 | 1 | 0.903 | 0.5 | 0 | site, file, b2 site, post | 1
1 | RFI-1147 | Southline Office | concrete, structural |  | B2 GL 12 TOW Threaded Rod Diameter Confirmation 1, RFI 1047 B2 GL 12 TOW Embed Remediation Question: There is rebar obstruction for full embedment of 1" threaded rod on TOW Embed Remediation fix on GL 12. See attached photo depicting the bars that are in question - protruding above the rest. Please co | RFI-1047 | Southline Office | concrete, structural |  | B2 Gridline 12 TOW Shearwall Embed Remediation 1, S5.3 Question: We can drill 4" OC between boundary elements on the Gridline 12 Shearwall as specified in the RFI-0963 - B2 Post Installed TOW Embeds in Lieu of Wet Set Embeds response. At the boundary elements, we will be able to drill with varying sp | 0.7595 | 1 | 0.9015 | 0.5 | 0 | tow embed, embed, remediation, photo, 12 tow, tow, embed remediation | 1
1 | RFI-1147 | Southline Office | concrete, structural |  | B2 GL 12 TOW Threaded Rod Diameter Confirmation 1, RFI 1047 B2 GL 12 TOW Embed Remediation Question: There is rebar obstruction for full embedment of 1" threaded rod on TOW Embed Remediation fix on GL 12. See attached photo depicting the bars that are in question - protruding above the rest. Please co | RFI-1047 | Southline Office | concrete, structural |  | B2 Gridline 12 TOW Shearwall Embed Remediation 1, S5.3 Question: We can drill 4" OC between boundary elements on the Gridline 12 Shearwall as specified in the RFI-0963 - B2 Post Installed TOW Embeds in Lieu of Wet Set Embeds response. At the boundary elements, we will be able to drill with varying sp | 0.7591 | 1 | 0.9003 | 0.5 | 0 | tow embed, embed, remediation, photo, 12 tow, tow, embed remediation | 1
1 | RFI-0533 | Southline Office | civil_site |  | Onsite - Drawing C4.2 updates - added sanitary sewer line | RFI-1274 | Southline Office | architectural, landscaping, civil_site | mep_rough_in | Per SI-05, Details 10/L8.02 and 10/L8.04 show perforated pipe for draingage below the linear LED (E13) within the concrete hardscape. This piping does not appear to be included in the site utility drawing C4.2 to tie into the storm drain system. Please provide an update to drawing C4.2 to incorporate the perforated pipe as shown in the landscaping details. | 0.7582 | 1 | 0.8973 | 0.5 | 0 | drawing c4, drawing, onsite, line | 1
1 | RFI-1153 | Southline Office | architectural | interior_finishes | Per email confirmation from DES on 11/20/23, please confirm it is acceptable to locate the tile base joint @ the midpoint of the floor tile (indicated in the updated drawing). | RFI-1698 | Southline Office | architectural | interior_finishes | B1 Exterior Penthouse Doors Threshold Confirmation 20 and detail 15/A9.22 Post on: 15/A9.22 Background: Due to the concrete curbs being poured short at the exterior doors in the North and South Penthouse, sill detail 15/A9.22 is n | 0.7582 | 0.95 | 0.7003 | 1 | 0 | acceptable, confirmation, des | 2
1 | RFI-0018 | Southline Office |  | structure | If we detail the 6 1/4" square plate washer per Detail-4/S5.43, then there is only 3/16" and 7/16" clearance from plate washer to column flange and Stiffener as shown in Model snippet-1. Please review and advise. If we detail a 3'-5" square embed plate and 3'-2" base plate per Detail-4/S5.43, then there is no weld shelf for a 3/8" fillet weld between the shear plate and embed plate as shown in Model snippet-2. Please review and advise. Per Detail-4/S5.43 3'-5" square embed plate is to be detaile | RFI-0965 | Southline Office |  | structure | PSD Added Cantilevered C12x25 Detail Clarification | 0.754 | 1 | 0.6334 | 1 | 0 | stud, embed, detail, connection, dimension, edge, shear | 4
1 | RFI-0018 | Southline Office |  | structure | If we detail the 6 1/4" square plate washer per Detail-4/S5.43, then there is only 3/16" and 7/16" clearance from plate washer to column flange and Stiffener as shown in Model snippet-1. Please review and advise. If we detail a 3'-5" square embed plate and 3'-2" base plate per Detail-4/S5.43, then there is no weld shelf for a 3/8" fillet weld between the shear plate and embed plate as shown in Model snippet-2. Please review and advise. Per Detail-4/S5.43 3'-5" square embed plate is to be detaile | RFI-0027 | Southline Office |  | structure | B1 Base plate stiffener projection at loading dock | 0.7539 | 1 | 0.7262 | 1 | 0 | base plate, plate, detail, connection, plate connection, model, marked, stiffener, base plate connection, column, follow, base | 4
1 | RFI-1720.1 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 POST TO: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 Please review the attached file. Per the responses to submittal #4540 Revs. 0-3, BART irrigation specs will differ from what is shown on the approved irrigation plans. BrightView requests an updated legend to reflect the correct BART irrigation components and where they are to be installed for field use. Please provide an updated L3.10 and L3.20 plan s | RFI-1653 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: 4/L3.10.1 POST TO: Site - Offsite Current Set: 4/L3.10.1 Please review the attached file. Per the BART Irrigation Legend and spec section 32 84 00, the master valve is not called out. Attached is a Superior Valves cut sheet. Please confirm if the master valve is adequate and if the valve is to be normally open or normally closed. | 0.7527 | 1 | 0.9681 | 0.5 | 0 | legend, file, site, irrigation, bart irrigation, offsite, sheet, post, bart | 1
1 | RFI-1153 | Southline Office | architectural | interior_finishes | Per email confirmation from DES on 11/20/23, please confirm it is acceptable to locate the tile base joint @ the midpoint of the floor tile (indicated in the updated drawing). | RFI-1839 | Southline Office | architectural | interior_finishes | B2 Servery WT-6 Tile Extent Confirmation 03, A10.01 Submittal #4905 Per detail 6b/A6.03 WT-6 is only to be installed on the sides of the mirrors. Per Submittal 4905 DES states that there is no tile behind the GL-2 mirrors. However, Finish Plan A10.01 shows the extent of WT-6 along entire wall. Please confirm | 0.7508 | 0.95 | 0.6711 | 1 | 0 | confirmation, des, tile | 4
1 | RFI-118 | CoreSite Data Center | fire_protection | preconstruction | At the West wall columns fireproofing will be within the plenum space below the raised access floor. Suggested answer Corgan, please confirm if the project needs to prevent monokote fireproofing form becoming air born within the plenum space. If so, please provide details for framing and drywall, or an alternative solution, such as a monokote sealer. | RFI-177 | CoreSite Data Center | architectural, fire_protection | preconstruction | The fire extinguisher cabinet specified for installation on the column adjacent to storage room 233 and staging room 232, does not fit due to dimensional constraints. To resolve this, DPR proposes relocating the cabinet to either the West wall of storage room 233, or the West wall of staging room 232. Suggested answer Corgan, please confirm which of these alternate locations is acceptable. | 0.7502 | 1 | 0.6747 | 1 | 0 | alternative, wall, west wall, form, west, suggested, corgan | 1
1 | RFI-1153 | Southline Office | architectural | interior_finishes | Per email confirmation from DES on 11/20/23, please confirm it is acceptable to locate the tile base joint @ the midpoint of the floor tile (indicated in the updated drawing). | RFI-1338 | Southline Office | architectural | interior_finishes | PSD Elevator Shaft Wall Paint Confirmation 01 Per the job walk on 01/30/2024 and the email correspondence between DES and DPR dated 01/18/2024, please confirm that painting all 4 walls of | 0.7502 | 1 | 0.7141 | 1 | 0 | acceptable, email, confirmation, des | 1
1 | RFI-0533 | Southline Office | civil_site |  | Onsite - Drawing C4.2 updates - added sanitary sewer line | RFI-1573 | Southline Office | concrete, plumbing, civil_site | foundation | REF: Site - Onsite Current Set: L8.06 POST TO: Site - Onsite Current Set: L8.06 Currently with what is excavated and graded for the sidewalk retaining wall by the B1 East side loading dock as shown on Detail 5/L8.06, there is a conflict with the 6” sanitary sewer that appears to penetrate the shear key at the bottom of the footing. There will be roughly 3” of clearance on top of the pipe and 6” below the bottom of pipe through the wall. Please provide rebar trim and penetration sleeve details fo | 0.7495 | 1 | 0.8663 | 0.5 | 0 | sanitary sewer, sanitary sewer line, sanitary, sewer, onsite, line, sewer line | 1
1 | RFI-0018 | Southline Office |  | structure | If we detail the 6 1/4" square plate washer per Detail-4/S5.43, then there is only 3/16" and 7/16" clearance from plate washer to column flange and Stiffener as shown in Model snippet-1. Please review and advise. If we detail a 3'-5" square embed plate and 3'-2" base plate per Detail-4/S5.43, then there is no weld shelf for a 3/8" fillet weld between the shear plate and embed plate as shown in Model snippet-2. Please review and advise. Per Detail-4/S5.43 3'-5" square embed plate is to be detaile | RFI-0016 | Southline Office |  | structure | B1 BRB Beam Cover Plate Split at Shear Plate | 0.744 | 1 | 0.6933 | 1 | 0 | fillet weld, fillet, plate, detail, shear plate, weld, follow, shear | 4
1 | RFI-118 | CoreSite Data Center | fire_protection | preconstruction | At the West wall columns fireproofing will be within the plenum space below the raised access floor. Suggested answer Corgan, please confirm if the project needs to prevent monokote fireproofing form becoming air born within the plenum space. If so, please provide details for framing and drywall, or an alternative solution, such as a monokote sealer. | RFI-99 | CoreSite Data Center | architectural | preconstruction | Could a furred wall be constructed at this location? | 0.7431 | 1 | 0.6556 | 1 | 0 | wall, west wall, form, west, suggested, corgan | 3
1 | RFI-1720.1 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 POST TO: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 Please review the attached file. Per the responses to submittal #4540 Revs. 0-3, BART irrigation specs will differ from what is shown on the approved irrigation plans. BrightView requests an updated legend to reflect the correct BART irrigation components and where they are to be installed for field use. Please provide an updated L3.10 and L3.20 plan s | RFI-1287 | Southline Office | civil_site, landscaping |  | The San Bruno Stamped Irrigation plans introduce BART irrigation legend on sheet L3.10.1. The symbols in this legend are identical to the symbols in the irrigation legend on sheet L3.00 but call for different model numbers. Please advise on the following questions: 1. Please confirm if the previously approved backflow, controller, and hydrometer are still approved and will be used throughout all Offsite Improvements. If not, and the BART irrigation legend is to be followed please clarify the fol | 0.7421 | 1 | 0.9371 | 0.5 | 0 | irrigation plans, plans, legend, site, plan, irrigation, bart irrigation, offsite, submit, sheet, use, bart, submittal | 2
1 | RFI-1720.1 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 POST TO: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 Please review the attached file. Per the responses to submittal #4540 Revs. 0-3, BART irrigation specs will differ from what is shown on the approved irrigation plans. BrightView requests an updated legend to reflect the correct BART irrigation components and where they are to be installed for field use. Please provide an updated L3.10 and L3.20 plan s | RFI-1782.1 | Southline Office | landscaping, electrical | mep_rough_in | REF: Site- Offsite Current Set: L3.30, L3.40 POST TO: Site- Offsite Current Set: L3.30, L3.40 Please review the attached file and forward this RFI to the City of SSF. Per the response to RFI 1782 offsite irrigation controllers along Southline avenue are not to be solar powered. Power will need to be run and tied in to controllers C & Z. Suggested answer DPR proposes running power to the controllers from city street light boxes with a transformer. Please confirm that this is acceptable. | 0.7414 | 1 | 0.8321 | 0.5 | 0 | file, site, irrigation, offsite, post | 1
1 | RFI-1892 | Southline Office | architectural, structural | foundation | B2 Floor Uniformity and Flatness Confirmation 3, Spec Sections 03-3000.3.6 Question: Per the Polished Concrete Mockup Review held on May 15th between PMA/DES/DPR, it was confirmed (see email attached) that the mockup reviewed was the final selection for the concrete uniformity and resolves any floor fl | RFI-22 | CoreSite Data Center | architectural | preconstruction | REFERENCE: P3-A09-03A/B - FINISH FLOOR PLAN - LEVEL TWO BACKGROUND: Finish floor at level 2 UPS rooms 241-245, Corridor 262, Mechanical Room 246, and the landing outside of Fire Riser 229 is called out as sealed concrete, SC-1, per Architectural finish floor plans. These are the only rooms that call for concrete sealer. However, no floor plan in the Architectural drawing set show these rooms as having the the hatching for SC-1 per the finish legend. Per 5/28/25 OAC, concrete sealer was already a | 0.7412 | 0.95 | 0.8622 | 0.7 | 0 | confirmation, concrete, floor | 1
1 | RFI-180 | CoreSite Data Center | interior_finishes | preconstruction | - Is powder coating the specified finish method? 3) Was the ceiling tile used in the previous phase a proprietary product? | ISSUE-20 | Abbott Alameda Office TI | flooring | preconstruction | Need to complete duct work to finish putting in act grid. Grid not straight Drawing: A2.2.2 (2ND FLOOR - REFLECTED CEILING PLAN) | 0.7393 | 1 | 0.7211 | 1 | 0 | ceiling tile, tile, ceiling, finish | 3
1 | RFI-1720.1 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 POST TO: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 Please review the attached file. Per the responses to submittal #4540 Revs. 0-3, BART irrigation specs will differ from what is shown on the approved irrigation plans. BrightView requests an updated legend to reflect the correct BART irrigation components and where they are to be installed for field use. Please provide an updated L3.10 and L3.20 plan s | RFI-1782 | Southline Office | electrical, landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.30, L3.40 POST TO: Site - Offsite Current Set: L3.00, L3.30, L3.40 Please review the attached file. 1) There is an unknown symbol on sheet L3.30 within the median. Please clarify this symbol. 2) The offsite irrigation legend provided in sheet L3.00 updated for SI-01 now calls for a conventional Baseline controller with a Baseline solar panel providing power. Baseline has said that the solar panel and hydrometer will only work on a 2-wire system. The cur | 0.7382 | 1 | 0.9161 | 0.5 | 0 | legend, brightview, file, site, irrigation, offsite, sheet, post | 1
1 | RFI-180 | CoreSite Data Center | interior_finishes | preconstruction | - Is powder coating the specified finish method? 3) Was the ceiling tile used in the previous phase a proprietary product? | ISSUE-53 | Abbott Alameda Office TI | flooring | preconstruction | Need to fix and finish installation of ACT Grid per approved DFOW. Drawing: A2.2.2 (2ND FLOOR - REFLECTED CEILING PLAN) | 0.7365 | 1 | 0.7113 | 1 | 0 | ceiling tile, tile, ceiling, finish | 3
1 | RFI-1147 | Southline Office | concrete, structural |  | B2 GL 12 TOW Threaded Rod Diameter Confirmation 1, RFI 1047 B2 GL 12 TOW Embed Remediation Question: There is rebar obstruction for full embedment of 1" threaded rod on TOW Embed Remediation fix on GL 12. See attached photo depicting the bars that are in question - protruding above the rest. Please co | RFI-1087 | Southline Office | concrete |  | B2 SikaTop Armatec at GL B and 12 Shearwalls 1 Question: Per RFIs 1047 and 1051 regarding the TOW embed remediation responses for GL B and 12, we are to drill holes to the TOW of GL 12 and face of wall on GL B in order to complete remediation measures. While field drilling these holes, we had a lot of | 0.7337 | 1 | 0.909 | 0.5 | 0 | tow embed, gl 12, embed, remediation, rebar, photo, tow embed remediation, tow, embed remediation | 1
1 | RFI-0533 | Southline Office | civil_site |  | Onsite - Drawing C4.2 updates - added sanitary sewer line | RFI-0793 | Southline Office | civil_site | mep_rough_in | Onsite - Domestic Water Tie in to PSD | 0.7312 | 1 | 0.8075 | 0.5 | 0 | drawing c4, drawing, onsite drawing, onsite, line, onsite drawing c4 | 2
1 | RFI-1720.1 | Southline Office | landscaping |  | REF: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 POST TO: Site - Offsite Current Set: L3.00, L3.10, L3.10.1, L3.10.2, L3.20 Please review the attached file. Per the responses to submittal #4540 Revs. 0-3, BART irrigation specs will differ from what is shown on the approved irrigation plans. BrightView requests an updated legend to reflect the correct BART irrigation components and where they are to be installed for field use. Please provide an updated L3.10 and L3.20 plan s | RFI-1811 | Southline Office | concrete, landscaping, lighting | foundation | REF: B2 Current Set: E8.01, Site - Onsite Current Set: L8.04 POST TO: B2 Current Set: E8.01, Site - Onsite Current Set: L8.04 Please review the attached file. Per detail 14/L8.04, LED bollard are to have rebar cages. However, detail 9/E8.01 on Sprig's electric drawings does not require a rebar cage for the same LED bollards. DPR suggests installing bollards without a rebar cage in their foundation as this was originally what was planned for. Please confirm this is acceptable. Please note, if reb | 0.7273 | 1 | 0.7852 | 0.5 | 0 | file, site, plan, post | 1
1 | RFI-1147 | Southline Office | concrete, structural |  | B2 GL 12 TOW Threaded Rod Diameter Confirmation 1, RFI 1047 B2 GL 12 TOW Embed Remediation Question: There is rebar obstruction for full embedment of 1" threaded rod on TOW Embed Remediation fix on GL 12. See attached photo depicting the bars that are in question - protruding above the rest. Please co | RFI-1091 | Southline Office | concrete, structural |  | B2 GL B and 12 TOW Embed Remediation Patchback Procedures 1, 4325-03-3000-0 B2 Quikcrete Grout Product Data, RFI 1087 B2 SikaTop Armatec at GL B and 12 Shearwalls Question: Please confirm the following patchback procedures are acceptable for the abandoned holes created from the TOW embed | 0.7247 | 1 | 0.8791 | 0.5 | 0 | 12 tow embed, tow embed, embed, b2 gl, remediation, embedment, rebar, rod, tow embed remediation, 12 tow, tow, embed remediation | 1
1 | RFI-180 | CoreSite Data Center | interior_finishes | preconstruction | - Is powder coating the specified finish method? 3) Was the ceiling tile used in the previous phase a proprietary product? | RFI-103 | CoreSite Data Center | interior_finishes, architectural | preconstruction | The Specified CT-1 material has been discontinued per the supplier. Below are some alternate options for approval. Samples are available upon request. Suggested answer Corgan, please review and select which option to proceed with | 0.7199 | 0.8 | 0.8112 | 1 | 0 | specified, tile | 1
1 | RFI-1537 | Southline Office |  | interior_finishes | B1 - D1 Lobby Light Fixture Layout | RFI-058 | Sutter Eden - Office TI |  | mep_trim_out | Architectural vs. Electrical Lighting RCP | 0.7181 | 1 | 0.6553 | 0.85 | 0 | light fixture, light, fixture, layout | 4
1 | RFI-0533 | Southline Office | civil_site |  | Onsite - Drawing C4.2 updates - added sanitary sewer line | RFI-1235 | Southline Office | civil_site | foundation | See drawing C4.1 in Onsite B2 Site Drawing Package: Currently we have 2 - 6" FW line and 1 - 15" SD line that is in conflict with the bioretention wall at the southwest corner of Building 1. See Detail 14/L8.05 & 1/L1.12A. DPR is planning to install FW and SD at the designed invert elevation(per plan). Please confirm if the footing and deepened edge(14/L8.05) is consistent throughout the whole span of the bioretention area. If so, please provide three penetration details to install the 2 - FW li | 0.715 | 1 | 0.7534 | 0.5 | 0 | drawing c4, drawing, onsite, line | 2
1 | RFI-0692 | Southline Office |  | interior_finishes | Offsite - Tanforan Utility Installation | RFI-2056 | Southline Office |  | mep_rough_in | Offsite - R20 Tanforan - 31 Tanforan Ave service connection 0 After contacting the property owner at 31 Tanforan: 1) There is no access from inside the garage to install the conduit/wiring shown. With the existing meter panel recessed mounted, removal of the existing stucco wall ma | 0.715 | 0.95 | 0.6939 | 0.7 | 0 | offsite, tanforan, installation | 4
1 | RFI-1537 | Southline Office |  | interior_finishes | B1 - D1 Lobby Light Fixture Layout | RFI-1877 | Southline Office | architectural | mep_trim_out | Ref: Submittal 4156, 4219, RFI 1351, 1362, A4.03 Per DES response to RFI 1362, the F22A type light fixtures should butt up against one another at their ends and align with a 3" offset from the face of the bar die. 1. Due to the bar being curved and the light fixtures being linear, please confirm 3" off set to be followed at center of light. 2. Please provide spacing and start point for F22A type fixtures. Please see attached for more information. | 0.7113 | 1 | 0.6481 | 0.85 | 0 | light fixture, light, fixture, layout | 4
1 | RFI-0040 | Southline Office |  | structure | B1 encased beam backup bar and weld at bottom flange | RFI-0005 | Southline Office | structural | structure | B1 Beam Connection @ GL-XB Reference: Herrick_SK_23A (attached) S2.02, S2.03, S2.04, S2.05, S2.06, S2.07, S5.40 Typical on floors 2 thru Roof, at the collector connection along GL-XB, between GL-18/GL-18.7. W14x22 beam is framing to beam W12x19 with eight(8) bolts per detail 7/S5.40 & 2/S5.40. However shear plate is projecting below the beam bottom flange, as shown in the model snippet attached. 1. Please review this steel connection and advise, typical condition on level 2 thru Roof. Ref | 0.7107 | 1 | 0.6523 | 1 | 0 | bottom, beam, flange, bottom flange | 4
1 | RFI-0862 | Southline Office | structural | foundation | B2 - Conduit Encasement Clarification | RFI-0349 | Southline Office | concrete, structural | foundation | PSD Detail for Vertical Penetrations Through Foundations Clarification | 0.7089 | 0.8 | 0.8096 | 1 | 0 | conduit, clarification | 1
1 | RFI-0862 | Southline Office | structural | foundation | B2 - Conduit Encasement Clarification | RFI-0349 | Southline Office | concrete, structural | foundation | PSD Detail for Vertical Penetrations Through Foundations Clarification | 0.7086 | 0.8 | 0.8088 | 1 | 0 | conduit, clarification | 1
1 | RFI-0533 | Southline Office | civil_site |  | Onsite - Drawing C4.2 updates - added sanitary sewer line | RFI-0866 | Southline Office | civil_site |  | Onsite - Fire Water Permit Question from Fire Marshal | 0.7082 | 0.95 | 0.789 | 0.5 | 0 | drawing, added, onsite | 1
1 | RFI-0108 | Southline Office | architectural, plumbing | mep_rough_in | B1 Drain and Cleanout Locations | RFI-1769 | Southline Office | architectural | envelope | B2 Trench Drain Waterproofing Details 01, A4.01, A9.40, Submittal 4086 B2 Floor Drains Question: Currently our trench drains do not have a clamp ring as shown at the circular drain locations in details 3 and 8 in A9.40. Please provide a detail advising how you would like us to terminate the waterproofing to th | 0.7003 | 0.8 | 0.8486 | 0.85 | 0 | drain, locations | 1
1 | RFI-1892 | Southline Office | architectural, structural | foundation | B2 Floor Uniformity and Flatness Confirmation 3, Spec Sections 03-3000.3.6 Question: Per the Polished Concrete Mockup Review held on May 15th between PMA/DES/DPR, it was confirmed (see email attached) that the mockup reviewed was the final selection for the concrete uniformity and resolves any floor fl | RFI-0784 | Southline Office | architectural, interior_finishes |  | DES to confirm it is acceptable to use the attached spec section for the interior concrete floor sealer per email conversation with Meg/DES on 08/02/23. | 0.698 | 1 | 0.79 | 0.5 | 0 | email, confirmation, concrete, spec, floor | 1
1 | RFI-0692 | Southline Office |  | interior_finishes | Offsite - Tanforan Utility Installation | RFI-2017 | Southline Office |  | mep_rough_in | Offsite - R20 Tanforan - 53 Tanforan service conversion 0 After contacting the property owner at 53 Tanforan Ave, AGL was able to access the 2 100A subpanels in the garage. These panels are side by side. The conductor cables installed between the 2 panels are installed without conduit | 0.6974 | 0.95 | 0.6374 | 0.7 | 0 | offsite, tanforan, installation | 4
1 | RFI-0692 | Southline Office |  | interior_finishes | Offsite - Tanforan Utility Installation | RFI-1993 | Southline Office |  | mep_rough_in | There is an question with the existing electrical panel conditions at 29 Tanforan. It appears the property owner has added conductors to the panel that are not in code and are non-permitted. All conductors to the panel should be inside the conduit. After contacting the property owner at 29 Tanforan Ave. it was discovered that the existing panel has conductor cables exposed and not protected. The cables do not appear to be connected to breaker and what it feeds is unknown. The installation of the | 0.6938 | 0.95 | 0.6259 | 0.7 | 0 | offsite, tanforan, installation | 4
1 | RFI-1892 | Southline Office | architectural, structural | foundation | B2 Floor Uniformity and Flatness Confirmation 3, Spec Sections 03-3000.3.6 Question: Per the Polished Concrete Mockup Review held on May 15th between PMA/DES/DPR, it was confirmed (see email attached) that the mockup reviewed was the final selection for the concrete uniformity and resolves any floor fl | RFI-144.1 | CoreSite Data Center | architectural, mechanical, electrical | preconstruction | At the north of corridor #0262, existing doors at floor slab level need to be shifted vertically upward by 3 feet 0 inches to match the raised access floor elevation. There is limited overhead space due to extensive existing and future installation, and raised access flooring in the corridor segment restricts room for installation 9' A.F.F. Please review and confirm if the following overhead installation configurations are acceptable. 1. Exit Sign Added @8' 0 1/8" from Raised Access Floor (CoreS | 0.6927 | 0.95 | 0.6927 | 0.7 | 0 | confirmation, concrete, floor | 1
1 | RFI-0108 | Southline Office | architectural, plumbing | mep_rough_in | B1 Drain and Cleanout Locations | RFI-0152 | Southline Office | architectural, plumbing |  | B1 Drain and Cleanout Elevation | 0.6924 | 0.8 | 1.0046 | 0.5 | 0 | drain, cleanout | 1
1 | RFI-1892 | Southline Office | architectural, structural | foundation | B2 Floor Uniformity and Flatness Confirmation 3, Spec Sections 03-3000.3.6 Question: Per the Polished Concrete Mockup Review held on May 15th between PMA/DES/DPR, it was confirmed (see email attached) that the mockup reviewed was the final selection for the concrete uniformity and resolves any floor fl | RFI-0700.1 | Southline Office | concrete | structure | Please confirm if the edge of the curb from G2 to G3 should align with the face of curb from G3 to G5 or if both of them should be 2' wide and not align. T1 Please confirm a 2' gap is sufficient for the drain located near the GC/G3 intersection. Tier 2: Please review the attached markup of the edge of slab and provide comments if the design intent does not match the markup. T2 Please confirm that the edge of the main slab between G13 and G14 will be 1' south of GC to align with the south face of | 0.6896 | 0.95 | 0.6452 | 0.85 | 0 | confirmation, concrete, floor | 4
1 | RFI-0040 | Southline Office |  | structure | B1 encased beam backup bar and weld at bottom flange | RFI-0033 | Southline Office |  | structure | is acceptable, Please confirm the same weld can be applied for stiffener to base plate in Detail-8/S5.43, as the stiffener to base plate weld is missing. 3. Detail-8/S5.43 does not show the weld details for stiffener to column flange. Please furnish the weld. 4. We understand that the Headed studs are to stop at concrete pedestal (top of Base plate to top of concrete pedestal). Please confirm or advise if these are required up to Level-1 Slab. 5. We understand that the 12" concrete perimeter cur | 0.6887 | 0.8 | 0.7423 | 1 | 0 | flange, weld | 4
1 | RFI-0108 | Southline Office | architectural, plumbing | mep_rough_in | B1 Drain and Cleanout Locations | RFI-1078 | Southline Office | architectural, structural, concrete | interior_finishes | Per coordination with Welker Bros and DES, please confirm it is acceptable to proceed with the construction specialties Pedigrid with recessed deep pit exterior WOM in lieu of the specified Forbo Nuway Tuftiguard on sheet If the proposed Construction Specialties Exterior WOM is acceptable, please update detail 16/ SK1 represents the proposed arrangement of the concrete sidewalk and the slab for the exterior walkoff mat. Please refer to SK1 and provide the additional information requested highlig | 0.6886 | 0.8 | 0.7985 | 0.7 | 0 | drain, locations | 1
1 | RFI-0108 | Southline Office | architectural, plumbing | mep_rough_in | B1 Drain and Cleanout Locations | RFI-2046 | Southline Office | architectural, plumbing, other |  | PSD Tier 1 Elevator Lobby Trench Drain Confirmation 01 Mark up PSD Tier 1 Lobby Pictures Site Drawing C4.2 At the elevator lobby on Tier 1, it was noticed that during heavy rain and wind events, water starts to accumulate under the sta | 0.6838 | 0.8 | 0.8657 | 0.5 | 0 | drain, locations | 1
1 | RFI-0040 | Southline Office |  | structure | B1 encased beam backup bar and weld at bottom flange | RFI-0019 | Southline Office |  | structure | B1 Stiffener plate to braced frame column weld clarification | 0.672 | 0.8 | 0.6865 | 1 | 0 | flange, weld | 4
1 | RFI-0108 | Southline Office | architectural, plumbing | mep_rough_in | B1 Drain and Cleanout Locations | RFI-1703 | Southline Office | architectural | interior_finishes | B2 Shower Room Tile Sloping 40 Question: Conflicting details 3 & 8/A9.40 show different sloping scenarios at trench drain locations. 1. Please confirm it is acceptable to slope the areas around the trench drains to continue to the shower drain as shown in the markup attached. 2. Please confirm T-2 tile cuts | 0.6636 | 0.8 | 0.803 | 0.7 | 0 | drain, locations | 1
1 | RFI-0862 | Southline Office | structural | foundation | B2 - Conduit Encasement Clarification | RFI-0236.2 | Southline Office | structural | structure | Please confirm that the chip and epoxy detail is acceptable as shown on sheet 2. Architect to confirm if loading dock starter wall is to terminate 2'-10" from Gridline 20 in relation to roll up door location. Please confirm if it is acceptable to demo existing poured starter wall to bottom of ramp at the loading dock. Please confirm size/dimension of plate and location of anchor bolts. The HSS support near the column encasement (Gridline U) will be at a higher elevation due to encasement elevati | 0.6579 | 0.8 | 0.7145 | 0.85 | 0 | encasement, clarification | 1
1 | RFI-251 | Silicon Valley Office |  | preconstruction | PAF Wall Framing Attachment to Structure | RFI-035 | Sutter Eden - Office TI | structural_steel | structure | Is it acceptable to attach the furring top track to the bottom of the soffit framing, as sketched? the furring need to be supported directly to the column or deck, or independently braced? | 0.6553 | 1 | 0.6277 | 0.5 | 0 | wall framing, framing, attachment, wall | 4
1 | RFI-1537 | Southline Office |  | interior_finishes | B1 - D1 Lobby Light Fixture Layout | RFI-1125 | Southline Office | electrical | mep_trim_out | B1 Site Lighting Updates per HLB Drawing | 0.6491 | 0.8 | 0.592 | 0.85 | 0 | light, layout | 4
1 | RFI-0862 | Southline Office | structural | foundation | B2 - Conduit Encasement Clarification | RFI-0775 | Southline Office | structural | foundation | B2 UG Conduit Conflict with Footing | 0.6489 | 0.5 | 0.9597 | 1 | 0 | conduit | 1
1 | RFI-0692 | Southline Office |  | interior_finishes | Offsite - Tanforan Utility Installation | RFI-2050 | Southline Office |  | mep_rough_in | Offsite - R20 Tanforan PGE and JT Drawing Clarification 0 Currently the JT plan page JT4.0 shows the conduits being stubbed out and ending before the Dollar Tanforan intersection (clouded in the attached plans.) However, the PGE plans, shows the spare conduit D6 going out and being stub | 0.6328 | 0.8 | 0.6889 | 0.7 | 0 | offsite, tanforan | 4
1 | RFI-0692 | Southline Office |  | interior_finishes | Offsite - Tanforan Utility Installation | RFI-1989 | Southline Office |  | mep_rough_in | Offsite - R20 Tanforan AT&T Conduit layout confirmation 0 The existing AT&T Manhole has 4 knockouts on each wall face. On the northern face of the manhole, the 4 knockouts are already in use with the conduits that were installed in the previous phase of R20 construction. The curre | 0.6322 | 0.8 | 0.6892 | 0.7 | 0 | offsite, tanforan | 4
1 | RFI-0862 | Southline Office | structural | foundation | B2 - Conduit Encasement Clarification | RFI-0576.4 | Southline Office | structural | structure | PSD Steel Beam Electrical Penetration Clarifications_R4 4 PSD Steel Beam Electrical Penetration Clarifications_R4 Reference: SLP1 - RFI 0576.4 - PSD Steel Beam Electrical Penetration Clarifications_R4 Background: After the submittal review for the PSD elevator and stair tower, Glazier Steel had follow-up questions. To avoid any delays in material procurement, DPR started a | 0.6312 | 0.8 | 0.6225 | 0.85 | 0 | conduit, clarification | 1
1 | RFI-189 | Silicon Valley Office |  | envelope | hole 3" to achieve 2 1/2" embedment on locations where 2 1/2" embedment cannot be achieved? | RFI-1894 | Southline Office | architectural |  | PSD Remediation for Depressed Bollard Embeds Confirmation 01.2024 Background: Prior to deck pours, bollard embeds were install | 0.6303 | 0.95 | 0.5179 | 0.5 | 0 | hole, locations, 1/2 | 4
1 | RFI-1537 | Southline Office |  | interior_finishes | B1 - D1 Lobby Light Fixture Layout | RFI-005 | Sutter Eden - Office TI |  | mep_trim_out | Lighting Controls Clarification | 0.6294 | 0.8 | 0.6085 | 0.85 | 0 | light, fixture | 4
1 | RFI-189 | Silicon Valley Office |  | envelope | hole 3" to achieve 2 1/2" embedment on locations where 2 1/2" embedment cannot be achieved? | RFI-1765 | Southline Office |  | structure | PSD Top of Ramp Rebar Clearance Remediation at Tiers 2-6 Confirmation 302 and S2.04 Attached Sealer Product Data Background: | 0.616 | 0.8 | 0.5675 | 0.85 | 0 | locations, 1/2 | 4
1 | RFI-189 | Silicon Valley Office |  | envelope | hole 3" to achieve 2 1/2" embedment on locations where 2 1/2" embedment cannot be achieved? | RFI-0006 | Southline Office | structural | foundation | B1 Anchor Bolt & Steel Base Plate Connection | 0.6156 | 0.95 | 0.5436 | 0.7 | 0 | hole, 1/2, embedment | 4
1 | RFI-1537 | Southline Office |  | interior_finishes | B1 - D1 Lobby Light Fixture Layout | RFI-2136.1 | Southline Office |  | interior_finishes | The low plaque wall behind B2 was poured to a maximum of 1'-9" above the north landscaping per detail 6/L8.02 with a thickness of 8". Now that the DG on the south side of the wall installed, the height from DG to the TOW is 1'-5". Per a conversation with DES, the desired elevation for TOW from DG is 1'-9". 1) In order to provide a uniform boardform finish around the wall while extending the height to 1'-9", the wall will need to extend 3" on all sides (see attached markup). Please confirm the ne | 0.5696 | 0.5 | 0.5746 | 1 | 0 | layout | 4
1 | RFI-189 | Silicon Valley Office |  | envelope | hole 3" to achieve 2 1/2" embedment on locations where 2 1/2" embedment cannot be achieved? | RFI-0799 | Southline Office | architectural, structural |  | B2 GS Girder Support at Concrete Wall Detail | 0.5568 | 0.8 | 0.5527 | 0.5 | 0 | hole, 1/2 | 4
1 | RFI-189 | Silicon Valley Office |  | envelope | hole 3" to achieve 2 1/2" embedment on locations where 2 1/2" embedment cannot be achieved? | RFI-0799 | Southline Office | architectural, structural |  | B2 GS Girder Support at Concrete Wall Detail | 0.5568 | 0.8 | 0.5528 | 0.5 | 0 | hole, 1/2 | 4
1 | RFI-184.1 | Silicon Valley Office |  | structure | Minimum Plywood Sheathing Dimension - Cycle 2 | RFI-1205 | Southline Office | concrete | structure | PSD Perimeter Column Clearance Clarification Columns are specified to have 2" bolsters on the face | 0.5464 | 0.5 | 0.618 | 1 | 0 | dimension | 4
1 | RFI-1030 | Southline Office | structural, architectural | structure | Do you have any recommendations? | RFI-0445 | Southline Office | civil_site, structural | foundation | B2 Micropile Testing Procedure | 0.5449 | 0.5 | 0.688 | 0.85 | 0 | recommendations | 1
1 | RFI-184.1 | Silicon Valley Office |  | structure | Minimum Plywood Sheathing Dimension - Cycle 2 | RFI-008 | Sutter Eden - Office TI |  | structure | Drywall Dimensions Clarification | 0.544 | 0.5 | 0.596 | 1 | 0 | dimension | 4
1 | RFI-184.1 | Silicon Valley Office |  | structure | Minimum Plywood Sheathing Dimension - Cycle 2 | RFI-1200 | Southline Office | concrete | structure | PSD Tier 4 GA/G2 Column Clearance Confirmation 04 Find attached the photo of the GA/G2 column at the upturn beam with dimensions for current coverage. This issue was caused by the capital that was leaning in for the EFCO formwork system. We rep | 0.5376 | 0.5 | 0.5886 | 1 | 0 | dimension | 4
1 | RFI-184.1 | Silicon Valley Office |  | structure | Minimum Plywood Sheathing Dimension - Cycle 2 | RFI-0008 | Southline Office | structural | structure | B1 Missing Steel Locating Dimensions | 0.5353 | 0.5 | 0.5809 | 1 | 0 | dimension | 4
1 | RFI-184.1 | Silicon Valley Office |  | structure | Minimum Plywood Sheathing Dimension - Cycle 2 | RFI-0003 | Southline Office | structural | structure | B1 Steel Beam to Column Bolt Edge Distance | 0.5118 | 0.5 | 0.5727 | 1 | 0 | minimum | 4
1 | RFI-251 | Silicon Valley Office |  | preconstruction | PAF Wall Framing Attachment to Structure | RFI-0033 | Southline Office |  | structure | is acceptable, Please confirm the same weld can be applied for stiffener to base plate in Detail-8/S5.43, as the stiffener to base plate weld is missing. 3. Detail-8/S5.43 does not show the weld details for stiffener to column flange. Please furnish the weld. 4. We understand that the Headed studs are to stop at concrete pedestal (top of Base plate to top of concrete pedestal). Please confirm or advise if these are required up to Level-1 Slab. 5. We understand that the 12" concrete perimeter cur | 0.4989 | 0.5 | 0.7097 | 0.5 | 0 | wall | 4
1 | RFI-251 | Silicon Valley Office |  | preconstruction | PAF Wall Framing Attachment to Structure | RFI-031 | Sutter Eden - Office TI |  | structure | be attached to the nearest low deck flute? | 0.4813 | 0.5 | 0.6317 | 0.5 | 0 | framing | 4
1 | RFI-0063 | Southline Office |  |  | B1 Waive shotcrete test panel requirement | RFI-0980 | Southline Office |  |  | Please review this location for conformance of shotcrete application. Due to the CMU wall dowel layout, some dowels have created contact lap splices with the back curtain of the fire water tank walls. This has been reviewed with the shotcrete subcontractor and they are confident regarding achieving consolidation at this area as it's at the back curtain only. Please confirm that these contact lap splices are acceptable. | 0.4784 | 0.5 | 0.6413 | 0.5 | 0 | shotcrete | 4
1 | RFI-0063 | Southline Office |  |  | B1 Waive shotcrete test panel requirement | RFI-0980 | Southline Office |  |  | Please review this location for conformance of shotcrete application. Due to the CMU wall dowel layout, some dowels have created contact lap splices with the back curtain of the fire water tank walls. This has been reviewed with the shotcrete subcontractor and they are confident regarding achieving consolidation at this area as it's at the back curtain only. Please confirm that these contact lap splices are acceptable. | 0.4783 | 0.5 | 0.6409 | 0.5 | 0 | shotcrete | 4
1 | RFI-251 | Silicon Valley Office |  | preconstruction | PAF Wall Framing Attachment to Structure | RFI-0016 | Southline Office |  | structure | B1 BRB Beam Cover Plate Split at Shear Plate | 0.4776 | 0.5 | 0.6388 | 0.5 | 0 | framing | 4
1 | RFI-251 | Silicon Valley Office |  | preconstruction | PAF Wall Framing Attachment to Structure | RFI-0799 | Southline Office | architectural, structural |  | B2 GS Girder Support at Concrete Wall Detail | 0.4738 | 0.5 | 0.626 | 0.5 | 0 | wall | 4
1 | RFI-0063 | Southline Office |  |  | B1 Waive shotcrete test panel requirement | RFI-1978.1 | Southline Office | concrete | commissioning | REF: Site - B2 Current Set: L8.06, Submittal #4856-1 Please forward to Tony Thompson for review. Please review the attached file. While the CMU wall foundation was being poured on 08/16/24, CTS inspector took cylinder samples of the concrete for compression testing. Compression testing at 28 days after the pour yielded a f'c of 4900 psi, which failed to meet design strength. Another compression test was performed 56 days after the pour and yielded a f'c of 5530 psi, which meets the design streng | 0.4626 | 0.5 | 0.5726 | 0.5 | 0 | test | 4
1 | RFI-0063 | Southline Office |  |  | B1 Waive shotcrete test panel requirement | RFI-0800 | Southline Office | concrete, architectural |  | The 215 note shown in several of the architectural drawings was changed from "non rated CMU wall" on SI-03 to "non rated shotcrete wall" See attached sheet | 0.4567 | 0.5 | 0.569 | 0.5 | 0 | shotcrete | 4
1 | RFI-0063 | Southline Office |  |  | B1 Waive shotcrete test panel requirement | RFI-0898 | Southline Office | architectural, structural | structure | Per discussions with Peter/DES and Jason/GPLA on 08/24, please confirm if it is acceptable to drill and epoxy Horz. Bars @ 4' O.C. for lateral support of the 6" CMU Wall. Please confirm size of horizontal bars and embedment depth. Per conversations with Jason/GPLA, please confirm that no CMU embeds are required for the 6" CMU Wall at either side of column GB/G2. | 0.4546 | 0.5 | 0.562 | 0.5 | 0 | panel | 4
1 | RFI-1030 | Southline Office | structural, architectural | structure | Do you have any recommendations? | RFI-1879 | Southline Office | architectural | structure | B2 Mod Bar Added Wall due to Plumbing Lines 03, A9.73 Question: Please see photos on the next page. Along 5 line just south of GL B/5 there are four plumbing pipes that are out of the Trimark food service die walls. It seems the best way to encase them into the bar drum is to build a new pony wall under | 0.4434 | 0 | 0.7534 | 1 | 0 |  | 3
1 | RFI-1030 | Southline Office | structural, architectural | structure | Do you have any recommendations? | RFI-0889 | Southline Office | structural, architectural | structure | Please advise if U-Edging should be stainless steel or carbon steel (blackened? How are the mesh panels to be fixed to the supporting steel? 51, is it still required? | 0.4408 | 0 | 0.8492 | 1 | 0 |  | 2
1 | RFI-1030 | Southline Office | structural, architectural | structure | Do you have any recommendations? | RFI-0017 | Southline Office | structural | structure | B1 Backup Bar and Run-off Tab Requirements for Moment and Framed Beams | 0.4369 | 0 | 0.8364 | 1 | 0 |  | 1
1 | RFI-1030 | Southline Office | structural, architectural | structure | Do you have any recommendations? | RFI-0017 | Southline Office | structural | structure | B1 Backup Bar and Run-off Tab Requirements for Moment and Framed Beams | 0.4369 | 0 | 0.8364 | 1 | 0 |  | 1